## Monitoring Point Locations
EPA Point 1 Discharge to waters
EPA Point 2 Total volume monitoring
EPA Point 3 Effluent quality monitoring

## 12-13
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 12/13
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | SS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/Day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | -
2012-06-01 | 2221 | [13 empty] | 3
2012-06-02 | 2858 | [13 empty] | 0
2012-06-03 | 2348 | [13 empty] | 0
2012-06-04 | 3104 | 0.22 | 0 | 6.8 | 0 | 2 | 0 | 2.9 | 0.13 | 0 | 9.3206 | 0 | 0.41782 | 6.428 | 0
2012-06-05 | 2468 | [13 empty] | 5
2012-06-06 | 2061 | [13 empty] | 3
2012-06-07 | 1835 | [13 empty] | 2
2012-06-08 | 2312 | [13 empty] | 6
2012-06-09 | 2612 | [13 empty] | 0
2012-06-10 | 2306 | [13 empty] | 1
2012-06-11 | 3270 | [13 empty] | 0
2012-06-12 | 6272 | [13 empty] | 0
2012-06-13 | 5218 | [13 empty] | 0
2012-06-14 | 4195 | [13 empty] | 0
2012-06-15 | 3278 | [13 empty] | 0
2012-06-16 | 2743 | [13 empty] | 0
2012-06-17 | 2553 | [13 empty] | 0
2012-06-18 | 2352 | 0.15 | 0 | 6.9 | 1 | 3 | 0 | 4.2 | 0.17 | 0 | 10.4118 | 0 | 0.42143 | 7.437 | 0
2012-06-19 | 2222 | [13 empty] | 0
2012-06-20 | 1826 | [13 empty] | 0
2012-06-21 | 2115 | [13 empty] | 0
2012-06-22 | 1943 | [13 empty] | 0
2012-06-23 | 1920 | [13 empty] | 0
2012-06-24 | 2097 | [13 empty] | 0
2012-06-25 | 1762 | [13 empty] | 0
2012-06-26 | 1967 | [13 empty] | 0
2012-06-27 | 1893 | [13 empty] | 0
2012-06-28 | 2903 | [13 empty] | 0
2012-06-29 | 4765 | [13 empty] | 0
2012-06-30 | 4647 | [13 empty] | 0
2012-07-01 | 3185 | [13 empty] | 0
2012-07-02 | 2648 | 0.32 | 0 | 6.8 | 0 | 3 | 0 | 3.4 | 0.13 | 0 | 9.3194 | 0 | 0.35633 | 8.223 | 0
2012-07-03 | 1993 | [13 empty] | 0
2012-07-04 | 2107 | [13 empty] | 0
2012-07-05 | 2251 | [13 empty] | 0
2012-07-06 | 1938 | [13 empty] | 0
2012-07-07 | 1766 | [13 empty] | 0
2012-07-08 | 2224 | [13 empty] | 0
2012-07-09 | 2339 | [13 empty] | 0
2012-07-10 | 2001 | [13 empty] | 0
2012-07-11 | 1686 | [13 empty] | 0
2012-07-12 | 1985 | [13 empty] | 0
2012-07-13 | 1857 | [13 empty] | 0
2012-07-14 | 1943 | [13 empty] | 0
2012-07-15 | 1861 | [13 empty] | 6
2012-07-16 | 1762 | 0.3 | 0 | 7 | 0 | 4 | 0 | 3.5 | 0.17 | 0 | 6.6325 | 0 | 0.32215 | 7.58 | 0
2012-07-17 | 1869 | [13 empty] | 0
2012-07-18 | 1626 | [13 empty] | 0
2012-07-19 | 1785 | [13 empty] | 0
2012-07-20 | 1420 | [13 empty] | 0
2012-07-21 | 1819 | [13 empty] | 0
2012-07-22 | 1562 | [13 empty] | 0
2012-07-23 | 1502 | [13 empty] | 0
2012-07-24 | 1411 | [13 empty] | 0
2012-07-25 | 1740 | [13 empty] | 0
2012-07-26 | 1544 | [13 empty] | 0
2012-07-27 | 1538 | [13 empty] | 0
2012-07-28 | 1340 | [13 empty] | 0
2012-07-29 | 1703 | [13 empty] | 0
2012-07-30 | 1453 | 0.4 | 0 | 6.9 | 0 | 4 | 0 | 3.8 | 0.16 | 0 | 6.1332 | 0 | 0.25824 | 6.456 | 0
2012-07-31 | 1334 | [13 empty] | 0
2012-08-01 | 1407 | [13 empty] | 0
2012-08-02 | 1397 | [13 empty] | 3
2012-08-03 | 1726 | [13 empty] | 0
2012-08-04 | 1398 | [13 empty] | 0
2012-08-05 | 1052 | [13 empty] | 0
2012-08-06 | 1555 | [13 empty] | 10
2012-08-07 | 1526 | [13 empty] | 0
2012-08-08 | 1318 | [13 empty] | 0
2012-08-09 | 1036 | [13 empty] | 0
2012-08-10 | 1613 | [13 empty] | 0
2012-08-11 | 1161 | [13 empty] | 0
2012-08-12 | 1316 | [13 empty] | 0
2012-08-13 | 1397 | 0.34 | 0 | 7 | 0 | 2 | 0 | 4.4 | 0.12 | 0 | 6.1204 | 0 | 0.16692 | 2.782 | 0
2012-08-14 | 1045 | [13 empty] | 0
2012-08-15 | 1409 | [13 empty] | 0
2012-08-16 | 1033 | [13 empty] | 0
2012-08-17 | 1103 | [13 empty] | 0
2012-08-18 | 985 | [13 empty] | 0
2012-08-19 | 1653 | [13 empty] | 0
2012-08-20 | 1262 | [13 empty] | 0
2012-08-21 | 1184 | [13 empty] | 0
2012-08-22 | 1212 | [13 empty] | 0
2012-08-23 | 1187 | [13 empty] | 0
2012-08-24 | 1203 | [13 empty] | 0
2012-08-25 | 987 | [13 empty] | 4
2012-08-26 | 1407 | [13 empty] | 8
2012-08-27 | 1209 | 0.5 | 0 | 7 | 2 | 7 | 0 | 3.8 | 0.16 | 0 | 5.0616 | 0 | 0.21312 | 9.324 | 0
2012-08-28 | 1131 | [13 empty] | 0
2012-08-29 | 1136 | [13 empty] | 0
2012-08-30 | 1154 | [13 empty] | 0
2012-08-31 | 1091 | [13 empty] | 0
2012-09-01 | 1216 | [13 empty] | 0
2012-09-02 | 1193 | [13 empty] | 0
2012-09-03 | 1197 | [13 empty] | 0
2012-09-04 | 1105 | [13 empty] | 0
2012-09-05 | 1121 | [13 empty] | 0
2012-09-06 | 1108 | [13 empty] | 0
2012-09-07 | 1081 | [13 empty] | 7
2012-09-08 | 759 | [13 empty] | 0
2012-09-09 | 1277 | [13 empty] | 0
2012-09-10 | 1108 | 0.29 | 0 | 6.9 | 0 | 3 | 0 | 5 | 0.14 | 0 | 6.06 | 0 | 0.16968 | 3.636 | 0
2012-09-11 | 1095 | [13 empty] | 0
2012-09-12 | 1081 | [13 empty] | 3
2012-09-13 | 1038 | [13 empty] | 3
2012-09-14 | 637 | [13 empty] | 2
2012-09-15 | 1447 | [13 empty] | 0
2012-09-16 | 1133 | [13 empty] | 0
2012-09-17 | 1056 | [13 empty] | 0
2012-09-18 | 748 | [13 empty] | 0
2012-09-19 | 1441 | [13 empty] | 0
2012-09-20 | 1145 | [13 empty] | 0
2012-09-21 | 1120 | [13 empty] | 0
2012-09-22 | 1132 | [13 empty] | 0
2012-09-23 | 1185 | [13 empty] | 0
2012-09-24 | 1210 | 1.1 | 0 | 7.1 | 3 | 4 | 0 | 4.3 | 0.19 | 0 | 5.2675 | 0 | 0.23275 | 4.9 | 24
2012-09-25 | 1173 | [13 empty] | 25
2012-09-26 | 1139 | [13 empty] | 0
2012-09-27 | 1167 | [13 empty] | 0
2012-09-28 | 1194 | [13 empty] | 0
2012-09-29 | 1178 | [13 empty] | 0
2012-09-30 | 1221 | [13 empty] | 11
2012-10-01 | 1195 | [13 empty] | 0
2012-10-02 | 1161 | [13 empty] | 95
2012-10-03 | 1150 | [13 empty] | 0
2012-10-04 | 1124 | [13 empty] | 0
2012-10-05 | 1101 | [13 empty] | 0
2012-10-06 | 1103 | [13 empty] | 0
2012-10-07 | 1081 | [13 empty] | 0
2012-10-08 | 1044 | 0.4 | 0 | 7.9 | 0 | 1 | 0 | 3.8 | 0.1 | 0 | 4.294 | 0 | 0.113 | 1.13 | 0
2012-10-09 | 833 | [13 empty] | 0
2012-10-10 | 1168 | [13 empty] | 0
2012-10-11 | 1257 | [13 empty] | 0
2012-10-12 | 1070 | [13 empty] | 0
2012-10-13 | 998 | [13 empty] | 0
2012-10-14 | 1052 | [13 empty] | 0
2012-10-15 | 1024 | [13 empty] | 0
2012-10-16 | 864 | [13 empty] | 0
2012-10-17 | 981 | [13 empty] | 0
2012-10-18 | 978 | [13 empty] | 12
2012-10-19 | 952 | [13 empty] | 0
2012-10-20 | 1043 | [13 empty] | 0
2012-10-21 | 1095 | [13 empty] | 0
2012-10-22 | 1097 | 0.21 | 0 | 7 | 0 | 4 | 0 | 4 | 0.1 | 0 | 4.484 | 0 | 0.1121 | 4.484 | 0
2012-10-23 | 1009 | [13 empty] | 0
2012-10-24 | 800 | [13 empty] | 0
2012-10-25 | 632 | [13 empty] | 7
2012-10-26 | 1315 | [13 empty] | 0
2012-10-27 | 981 | [13 empty] | 8
2012-10-28 | 769 | [13 empty] | 0
2012-10-29 | 1328 | [13 empty] | 0
2012-10-30 | 622 | [13 empty] | 0
2012-10-31 | 944 | [13 empty] | 0
2012-11-01 | 1164 | [13 empty] | 0
2012-11-02 | 970 | [13 empty] | 27
2012-11-03 | 980 | [13 empty] | 0
2012-11-04 | 712 | [13 empty] | 0
2012-11-05 | 953 | 0.36 | 0 | 7.4 | 2 | 3 | 0 | 5 | 0.11 | 0 | 5.17 | 0 | 0.11374 | 3.102 | 31
2012-11-06 | 1027 | [13 empty] | 0
2012-11-07 | 970 | [13 empty] | 0
2012-11-08 | 926 | [13 empty] | 0
2012-11-09 | 1217 | [13 empty] | 6
2012-11-10 | 1019 | [13 empty] | 0
2012-11-11 | 1063 | [13 empty] | 0
2012-11-12 | 1342 | [13 empty] | 0
2012-11-13 | 1059 | [13 empty] | 0
2012-11-14 | 1052 | [13 empty] | 0
2012-11-15 | 706 | [13 empty] | 0
2012-11-16 | 1368 | [13 empty] | 0
2012-11-17 | 1058 | [13 empty] | 0
2012-11-18 | 1402 | [13 empty] | 0
2012-11-19 | 1747 | 0.81 | 2 | 7 | 26 | 10 | 0 | 2.9 | 0.2 | 0 | 3.1407 | 2.166 | 0.2166 | 10.83 | 0
2012-11-20 | 1409 | [13 empty] | 0
2012-11-21 | 955 | [13 empty] | 0
2012-11-22 | 1336 | [13 empty] | 0
2012-11-23 | 1476 | [13 empty] | 0
2012-11-24 | 1288 | [13 empty] | 0
2012-11-25 | 1188 | [13 empty] | 0
2012-11-26 | 894 | [13 empty] | 0
2012-11-27 | 1420 | [13 empty] | 0
2012-11-28 | 1136 | [13 empty] | 0
2012-11-29 | 1123 | [13 empty] | 4
2012-11-30 | 1046 | [13 empty] | 0
2012-12-01 | 1073 | [13 empty] | 0
2012-12-02 | 1113 | [13 empty] | 0
2012-12-03 | 1095 | 0.27 | 0 | 7 | 2 | 7 | 0 | 3.7 | 0.1 | 0 | 4.1699 | 0 | 0.1127 | 7.889 | 6
2012-12-04 | 1079 | [13 empty] | 13
2012-12-05 | 1017 | [13 empty] | 2
2012-12-06 | 1049 | [13 empty] | 2
2012-12-07 | 1010 | [13 empty] | 0
2012-12-08 | 1045 | [13 empty] | 2
2012-12-09 | 1041 | [13 empty] | 5
2012-12-10 | 1059 | [13 empty] | 4
2012-12-11 | 981 | [13 empty] | 45
2012-12-12 | 1260 | [13 empty] | 136
2012-12-13 | 1055 | [13 empty] | 25
2012-12-14 | 1104 | [13 empty] | 0
2012-12-15 | 982 | [13 empty] | 4
2012-12-16 | 1299 | [13 empty] | 0
2012-12-17 | 1044 | 0.38 | 0 | 7.3 | 6 | 3 | 0 | 2.7 | 0.14 | 0 | 2.943 | 0 | 0.1526 | 3.27 | 0
2012-12-18 | 980 | [13 empty] | 6
2012-12-19 | 915 | [13 empty] | 0
2012-12-20 | 1261 | [13 empty] | 0
2012-12-21 | 1261 | [13 empty] | 6
2012-12-22 | 1727 | [13 empty] | 0
2012-12-23 | 1137 | [13 empty] | 13
2012-12-24 | 1561 | [13 empty] | 18
2012-12-25 | 1485 | [13 empty] | 0
2012-12-26 | 863 | [13 empty] | 0
2012-12-27 | 1472 | [13 empty] | 0
2012-12-28 | 1556 | [13 empty] | 14
2012-12-29 | 1271 | [13 empty] | 0
2012-12-30 | 1450 | [13 empty] | 19
2012-12-31 | 1616 | 2.1 | 0 | 7.4 | 9 | 2 | 2 | 5 | 0.24 | 3.106 | 7.765 | 0 | 0.37272 | 3.106 | 3
2013-01-01 | 1250 | [13 empty] | 6
2013-01-02 | 1585 | [13 empty] | 8
2013-01-03 | 1361 | [13 empty] | 80
2013-01-04 | 1311 | [13 empty] | 20
2013-01-05 | 1422 | [13 empty] | 13
2013-01-06 | 984 | [13 empty] | 20
2013-01-07 | 1528 | [13 empty] | 96
2013-01-08 | 966 | [13 empty] | 20
2013-01-09 | 1460 | [13 empty] | 21
2013-01-10 | 1375 | [13 empty] | 3
2013-01-11 | 1166 | [13 empty] | 7
2013-01-12 | 1600 | [13 empty] | 9
2013-01-13 | 1067 | [13 empty] | 0
2013-01-14 | 1244 | 0.51 | 0 | 7.2 | 9 | 6 | 0 | 4.5 | 0.25 | 0 | 5.949 | 0 | 0.3305 | 7.932 | 25
2013-01-15 | 1576 | [13 empty] | 50
2013-01-16 | 1198 | [13 empty] | 25
2013-01-17 | 1226 | [13 empty] | 3
2013-01-18 | 991 | [13 empty] | 0
2013-01-19 | 1520 | [13 empty] | 0
2013-01-20 | 1156 | [13 empty] | 0
2013-01-21 | 1122 | [13 empty] | 4
2013-01-22 | 1114 | [13 empty] | 3
2013-01-23 | 1024 | [13 empty] | 0
2013-01-24 | 1095 | [13 empty] | 0
2013-01-25 | 1307 | [13 empty] | 1
2013-01-26 | 1119 | [13 empty] | 0
2013-01-27 | 1614 | [13 empty] | 0
2013-01-28 | 1740 | 0.23 | 0 | 7.1 | 4 | 2 | 0 | 2.4 | 0.24 | 0 | 5.88 | 0 | 0.588 | 4.9 | 0
2013-01-29 | 3853 | [13 empty] | 0
2013-01-30 | 4049 | [13 empty] | 8
2013-01-31 | 3184 | [13 empty] | 0
2013-02-01 | 1958 | [13 empty] | 0
2013-02-02 | 1921 | [13 empty] | 0
2013-02-03 | 1477 | [13 empty] | 0
2013-02-04 | 1470 | [13 empty] | 0
2013-02-05 | 1549 | [13 empty] | 0
2013-02-06 | 1313 | [13 empty] | 0
2013-02-07 | 1491 | [13 empty] | 0
2013-02-08 | 2279 | [13 empty] | 0
2013-02-09 | 1688 | [13 empty] | 0
2013-02-10 | 1551 | [13 empty] | 7
2013-02-11 | 1470 | 0.38 | 0 | 7.2 | 0 | 6 | 0 | 3.1 | 0.11 | 0 | 4.5415 | 0 | 0.16115 | 8.79 | 0
2013-02-12 | 1440 | [13 empty] | 0
2013-02-13 | 1350 | [13 empty] | 30
2013-02-14 | 1445 | [13 empty] | 0
2013-02-15 | 1629 | [13 empty] | 0
2013-02-16 | 1396 | [13 empty] | 7
2013-02-17 | 1666 | [13 empty] | 39
2013-02-18 | 1698 | [13 empty] | 10
2013-02-19 | 1789 | [13 empty] | 9
2013-02-20 | 4616 | [13 empty] | 4
2013-02-21 | 3437 | [13 empty] | 0
2013-02-22 | 2927 | [13 empty] | 49
2013-02-23 | 5349 | [13 empty] | 0
2013-02-24 | 4872 | [13 empty] | 0
2013-02-25 | 3944 | 0.36 | 0 | 6.8 | 0 | 14 | 0 | 2.7 | 0.45 | 0 | 11.2077 | 0 | 1.8679 | 58.114 | 26
2013-02-26 | 3661 | [13 empty] | 20
2013-02-27 | 2943 | [13 empty] | 0
2013-02-28 | 2620 | [13 empty] | 0
2013-03-01 | 2382 | [13 empty] | 95
2013-03-02 | 2329 | [13 empty] | 0
2013-03-03 | 5002 | [13 empty] | 0
2013-03-04 | 5871 | [13 empty] | 0
2013-03-05 | 4029 | [13 empty] | 0
2013-03-06 | 3031 | [13 empty] | 0
2013-03-07 | 2832 | [13 empty] | 0
2013-03-08 | 2646 | [13 empty] | 0
2013-03-09 | 2232 | [13 empty] | 0
2013-03-10 | 2350 | [13 empty] | 0
2013-03-11 | 2013 | 0.26 | 0 | 7 | 1 | 5 | 0 | 3.9 | 0.24 | 0 | 8.7087 | 0 | 0.53592 | 11.165 | 0
2013-03-12 | 1910 | [13 empty] | 0
2013-03-13 | 2555 | [13 empty] | 0
2013-03-14 | 2248 | [13 empty] | 0
2013-03-15 | 2121 | [13 empty] | 0
2013-03-16 | 1816 | [13 empty] | 0
2013-03-17 | 1862 | [13 empty] | 4
2013-03-18 | 1503 | [13 empty] | 0
2013-03-19 | 2234 | [13 empty] | 3
2013-03-20 | 1391 | [13 empty] | 1
2013-03-21 | 1601 | [13 empty] | 0
2013-03-22 | 1699 | [13 empty] | 34
2013-03-23 | 2000 | [13 empty] | 0
2013-03-24 | 1642 | [13 empty] | 0
2013-03-25 | 1318 | 0.4 | 0 | 7 | 100 | 1 | 0 | 3.7 | 0.11 | 0 | 5.9237 | 0 | 0.17611 | 1.601 | 18
2013-03-26 | 1300 | [13 empty] | 3
2013-03-27 | 1919 | [13 empty] | 0
2013-03-28 | 1940 | [13 empty] | 0
2013-03-29 | 1500 | [13 empty] | 2
2013-03-30 | 1446 | [13 empty] | 0
2013-03-31 | 1606 | [13 empty] | 0
2013-04-01 | 1912 | [13 empty] | 0
2013-04-02 | 1838 | [13 empty] | 0
2013-04-03 | 1898 | [13 empty] | 0
2013-04-04 | 1342 | [13 empty] | 0
2013-04-05 | 2155 | [13 empty] | 0
2013-04-06 | 2425 | [13 empty] | 4
2013-04-07 | 2440 | [13 empty] | 35
2013-04-08 | 2290 | 0.33 | 0 | 7 | 1 | 4 | 0 | 3.8 | 0.08 | 0 | 9.6748 | 0 | 0.20368 | 10.184 | 1
2013-04-09 | 2026 | [13 empty] | 1
2013-04-10 | 2304 | [13 empty] | 0
2013-04-11 | 3211 | [13 empty] | 2
2013-04-12 | 2183 | [13 empty] | 0
2013-04-13 | 2804 | [13 empty] | 6
2013-04-14 | 3337 | [13 empty] | 0
2013-04-15 | 2827 | [13 empty] | 0
2013-04-16 | 2051 | [13 empty] | 0
2013-04-17 | 2657 | [13 empty] | 25
2013-04-18 | 4440 | [13 empty] | 0
2013-04-19 | 2907 | [13 empty] | 0
2013-04-20 | 2585 | [13 empty] | 0
2013-04-21 | 2116 | [13 empty] | 0
2013-04-22 | 2202 | 0.31 | 0 | 7.1 | 0 | 3 | 0 | 4.1 | 0.09 | 0 | 9.5653 | 0 | 0.20997 | 6.999 | 0
2013-04-23 | 2136 | [13 empty] | 0
2013-04-24 | 2064 | [13 empty] | 0
2013-04-25 | 2198 | [13 empty] | 0
2013-04-26 | 1685 | [13 empty] | 0
2013-04-27 | 2122 | [13 empty] | 0
2013-04-28 | 1849 | [13 empty] | 0
2013-04-29 | 1341 | [13 empty] | 0
2013-04-30 | 2093 | [13 empty] | 0
2013-05-01 | 1652 | [13 empty] | 0
2013-05-02 | 1626 | [13 empty] | 0
2013-05-03 | 1363 | [13 empty] | 0
2013-05-04 | 1823 | [13 empty] | 0
2013-05-05 | 1505 | [13 empty] | 0
2013-05-06 | 1424 | 0.27 | 0 | 7 | 0 | 7 | 0 | 3.9 | 0.16 | 0 | 6.1425 | 0 | 0.252 | 11.025 | 0
2013-05-07 | 1522 | [13 empty] | 0
2013-05-08 | 1781 | [13 empty] | 0
2013-05-09 | 1591 | [13 empty] | 0
2013-05-10 | 1522 | [13 empty] | 0
2013-05-11 | 2149 | [13 empty] | 0
2013-05-12 | 2080 | [13 empty] | 0
2013-05-13 | 1628 | [13 empty] | 0
2013-05-14 | 1514 | [13 empty] | 0
2013-05-15 | 1646 | [13 empty] | 0
2013-05-16 | 1834 | [13 empty] | 0
2013-05-17 | 1347 | [13 empty] | 0
2013-05-18 | 1542 | [13 empty] | 0
2013-05-19 | 1737 | [13 empty] | 10
2013-05-20 | 1438 | 0.31 | 0 | 6.8 | 6 | 15 | 2 | 4.8 | 0.44 | 3.396 | 8.1504 | 0 | 0.74712 | 25.47 | 0
2013-05-21 | 1306 | [13 empty] | 0
2013-05-22 | 1395 | [13 empty] | 0
2013-05-23 | 1375 | [13 empty] | 0
2013-05-24 | 1406 | [13 empty] | 0
2013-05-25 | 1704 | [13 empty] | 0
2013-05-26 | 1927 | [13 empty] | 0
2013-05-27 | 1548 | [13 empty] | 0
2013-05-28 | 1382 | [13 empty] | 0
2013-05-29 | 1582 | [13 empty] | 0
2013-05-30 | 1509 | [13 empty] | 5
2013-05-31 | 1461 | [13 empty] | 0
MINIMUM | 622 | 0.15 | 0 | 6.8 | 0 | 1 | 0 | 2.4 | 0.08 | 0 | 2.943 | 0 | 0.1121 | 1.13 | 0
AVERAGE | 1693.5205 | 0.44269 | 0.076923 | 7.0615 | 6.6154 | 4.8077 | 0.15385 | 3.8192 | 0.17423 | 0.25008 | 6.6168 | 0.083308 | 0.3394 | 9.106 | 4.1397
MAXIMUM | 6272 | 2.1 | 2 | 7.9 | 100 | 15 | 2 | 5 | 0.45 | 3.396 | 11.2077 | 2.166 | 1.8679 | 58.114 | 136
[9 empty] | Total | 6.502 | 172.0372 | 2.166 | 8.8243 | 236.757 | 1511
| SAMPLE COUNT | 25

## 13-14
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 13/14
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | SS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| ML/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | -
2013-06-01 | 1496 | [13 empty] | 0
2013-06-02 | 1672 | [13 empty] | 0
2013-06-03 | 1422 | [13 empty] | 3
2013-06-04 | 1294 | 0.23 | 2 | 6.9 | 2 | 8 | 2 | 4.1 | 0.22 | 3.184 | 6.5272 | 3.184 | 0.35024 | 12.736 | 4
2013-06-05 | 1620 | [13 empty] | 0
2013-06-06 | 1333 | [13 empty] | 0
2013-06-07 | 1500 | [13 empty] | 2
2013-06-08 | 1072 | [13 empty] | 0
2013-06-09 | 1353 | [13 empty] | 1
2013-06-10 | 1563 | [13 empty] | 0
2013-06-11 | 1512 | [13 empty] | 3
2013-06-12 | 1227 | [13 empty] | 8
2013-06-13 | 2026 | [13 empty] | 0
2013-06-14 | 1888 | [13 empty] | 18
2013-06-15 | 1285 | [13 empty] | 0
2013-06-16 | 1607 | [13 empty] | 0
2013-06-17 | 1357 | [13 empty] | 0
2013-06-18 | 1098 | 3.9 | 2 | 6.8 | 10 | 5 | 2 | 7.7 | 0.23 | 3.198 | 12.3123 | 3.198 | 0.36777 | 7.995 | 0
2013-06-19 | 1904 | [13 empty] | 0
2013-06-20 | 1399 | [13 empty] | 0
2013-06-21 | 1172 | [13 empty] | 0
2013-06-22 | 541 | [13 empty] | 0
2013-06-23 | 712 | [13 empty] | 4
2013-06-24 | 833 | [13 empty] | 0
2013-06-25 | 2178 | [13 empty] | 0
2013-06-26 | 1237 | [13 empty] | 0
2013-06-27 | 1301 | [13 empty] | 0
2013-06-28 | 1462 | [13 empty] | 0
2013-06-29 | 2014 | [13 empty] | 23
2013-06-30 | 1889 | [13 empty] | 23
2013-07-01 | 2006 | [13 empty] | 14
2013-07-02 | 3177 | 1.7 | 2 | 6.7 | 13 | 18 | 2 | 8.9 | 0.47 | 3.9 | 17.355 | 3.9 | 0.9165 | 35.1 | 49
2013-07-03 | 2560 | [13 empty] | 28
2013-07-04 | 2546 | [13 empty] | 11
2013-07-05 | 2315 | [13 empty] | 0
2013-07-06 | 1765 | [13 empty] | 0
2013-07-07 | 1780 | [13 empty] | 0
2013-07-08 | 1936 | [13 empty] | 0
2013-07-09 | 1876 | [13 empty] | 0
2013-07-10 | 1373 | [13 empty] | 0
2013-07-11 | 1793 | [13 empty] | 16
2013-07-12 | 2689 | [13 empty] | 15
2013-07-13 | 2355 | [13 empty] | 13
2013-07-14 | 1881 | [13 empty] | 0
2013-07-15 | 1809 | [13 empty] | 0
2013-07-16 | 1703 | 0.47 | 2 | 6.6 | 4 | 16 | 2 | 4.1 | 0.34 | 3.894 | 7.9827 | 3.894 | 0.66198 | 31.152 | 0
2013-07-17 | 1619 | [13 empty] | 0
2013-07-18 | 1608 | [13 empty] | 0
2013-07-19 | 1371 | [13 empty] | 0
2013-07-20 | 1736 | [13 empty] | 2
2013-07-21 | 1634 | [13 empty] | 0
2013-07-22 | 1593 | [13 empty] | 12
2013-07-23 | 923 | [13 empty] | 6
2013-07-24 | 1924 | [13 empty] | 0
2013-07-25 | 1375 | [13 empty] | 0
2013-07-26 | 1383 | [13 empty] | 0
2013-07-27 | 1452 | [13 empty] | 0
2013-07-28 | 1628 | [13 empty] | 0
2013-07-29 | 1446 | [13 empty] | 0
2013-07-30 | 1230 | 0.94 | 2 | 6.6 | 3 | 11 | 4 | 4.3 | 0.25 | 5.884 | 6.3253 | 2.942 | 0.36775 | 16.181 | 3
2013-07-31 | 1696 | [13 empty] | 0
2013-08-01 | 1024 | [13 empty] | 2
2013-08-02 | 1689 | [13 empty] | 0
2013-08-03 | 1399 | [13 empty] | 0
2013-08-04 | 1255 | [13 empty] | 0
2013-08-05 | 1166 | [13 empty] | 0
2013-08-06 | 1644 | [13 empty] | 0
2013-08-07 | 1074 | [13 empty] | 0
2013-08-08 | 1734 | [13 empty] | 0
2013-08-09 | 1384 | [13 empty] | 0
2013-08-10 | 1362 | [13 empty] | 0
2013-08-11 | 1329 | [13 empty] | 0
2013-08-12 | 1318 | [13 empty] | 0
2013-08-13 | 1158 | 0.85 | 2 | 7 | 4 | 5 | 2 | 5.9 | 0.15 | 2.38 | 7.021 | 2.38 | 0.1785 | 5.95 | 0
2013-08-14 | 1218 | [13 empty] | 0
2013-08-15 | 1082 | [13 empty] | 0
2013-08-16 | 1439 | [13 empty] | 10
2013-08-17 | 1183 | [13 empty] | 0
2013-08-18 | 1279 | [13 empty] | 0
2013-08-19 | 1225 | [13 empty] | 0
2013-08-20 | 1164 | [13 empty] | 0
2013-08-21 | 730 | [13 empty] | 0
2013-08-22 | 1541 | [13 empty] | 0
2013-08-23 | 1319 | [13 empty] | 0
2013-08-24 | 1215 | [13 empty] | 0
2013-08-25 | 986 | [13 empty] | 0
2013-08-26 | 1698 | [13 empty] | 0
2013-08-27 | 1372 | 0.67 | 2 | 7 | 10 | 7 | 2 | 5.1 | 0.18 | 2.504 | 6.3852 | 2.504 | 0.22536 | 8.764 | 0
2013-08-28 | 1188 | [13 empty] | 0
2013-08-29 | 1187 | [13 empty] | 0
2013-08-30 | 1198 | [13 empty] | 0
2013-08-31 | 1201 | [13 empty] | 0
2013-09-01 | 1230 | [13 empty] | 0
2013-09-02 | 1263 | [13 empty] | 0
2013-09-03 | 1138 | [13 empty] | 0
2013-09-04 | 1121 | [13 empty] | 0
2013-09-05 | 1115 | [13 empty] | 0
2013-09-06 | 1180 | [13 empty] | 0
2013-09-07 | 1165 | [13 empty] | 0
2013-09-08 | 1146 | [13 empty] | 0
2013-09-09 | 1192 | [13 empty] | 0
2013-09-10 | 1107 | 0.26 | 2 | 7.2 | 1 | 5 | 2 | 4.9 | 0.13 | 2.256 | 5.5272 | 2.256 | 0.14664 | 5.64 | 0
2013-09-11 | 708 | [13 empty] | 0
2013-09-12 | 1388 | [13 empty] | 0
2013-09-13 | 1112 | [13 empty] | 0
2013-09-14 | 1254 | [13 empty] | 0
2013-09-15 | 1137 | [13 empty] | 0
2013-09-16 | 1167 | [13 empty] | 0
2013-09-17 | 1221 | [13 empty] | 0
2013-09-18 | 1603 | [13 empty] | 50
2013-09-19 | 1303 | [13 empty] | 0
2013-09-20 | 1246 | [13 empty] | 0
2013-09-21 | 1082 | [13 empty] | 0
2013-09-22 | 1114 | [13 empty] | 0
2013-09-23 | 1616 | [13 empty] | 0
2013-09-24 | 932 | 0.57 | 2 | 7.1 | 8 | 4 | 2 | 5.3 | 0.17 | 2.606 | 6.9059 | 2.606 | 0.22151 | 5.212 | 0
2013-09-25 | 1292 | [13 empty] | 0
2013-09-26 | 1273 | [13 empty] | 0
2013-09-27 | 1468 | [13 empty] | 0
2013-09-28 | 1095 | [13 empty] | 0
2013-09-29 | 1251 | [13 empty] | 0
2013-09-30 | 1274 | [13 empty] | 0
2013-10-01 | 1546 | [13 empty] | 0
2013-10-02 | 1207 | [13 empty] | 0
2013-10-03 | 879 | [13 empty] | 0
2013-10-04 | 1586 | [13 empty] | 0
2013-10-05 | 1258 | [13 empty] | 0
2013-10-06 | 1120 | [13 empty] | 0
2013-10-07 | 1253 | [13 empty] | 0
2013-10-08 | 1281 | 0.79 | 2 | 7.4 | 4 | 3 | 2 | 6.7 | 0.21 | 2.592 | 8.6832 | 2.592 | 0.27216 | 3.888 | 0
2013-10-09 | 1160 | [13 empty] | 0
2013-10-10 | 1128 | [13 empty] | 0
2013-10-11 | 1081 | [13 empty] | 0
2013-10-12 | 1141 | [13 empty] | 0
2013-10-13 | 1326 | [13 empty] | 0
2013-10-14 | 848 | [13 empty] | 0
2013-10-15 | 1369 | [13 empty] | 0
2013-10-16 | 1111 | [13 empty] | 0
2013-10-17 | 1111 | [13 empty] | 0
2013-10-18 | 1103 | [13 empty] | 0
2013-10-19 | 1093 | [13 empty] | 0
2013-10-20 | 1113 | [13 empty] | 0
2013-10-21 | 1165 | [13 empty] | 6
2013-10-22 | 1046 | 0.24 | 2 | 7.3 | 1 | 9 | 2 | 9.8 | 0.25 | 2.092 | 10.2508 | 2.092 | 0.2615 | 9.414 | 0
2013-10-23 | 1096 | [13 empty] | 0
2013-10-24 | 1159 | [13 empty] | 0
2013-10-25 | 1056 | [13 empty] | 0
2013-10-26 | 1176 | [13 empty] | 0
2013-10-27 | 1098 | [13 empty] | 0
2013-10-28 | 1096 | [13 empty] | 0
2013-10-29 | 1122 | [13 empty] | 0
2013-10-30 | 518 | [13 empty] | 3
2013-10-31 | 1167 | [13 empty] | 0
2013-11-01 | 1299 | [13 empty] | 0
2013-11-02 | 827 | [13 empty] | 0
2013-11-03 | 1547 | [13 empty] | 0
2013-11-04 | 1120 | [13 empty] | 0
2013-11-05 | 1050 | 0.23 | 2 | 7.3 | 3 | 6 | 2 | 6.1 | 0.18 | 2.242 | 6.8381 | 2.242 | 0.20178 | 6.726 | 0
2013-11-06 | 1051 | [13 empty] | 0
2013-11-07 | 654 | [13 empty] | 0
2013-11-08 | 1349 | [13 empty] | 0
2013-11-09 | 878 | [13 empty] | 0
2013-11-10 | 1099 | [13 empty] | 0
2013-11-11 | 1702 | [13 empty] | 0
2013-11-12 | 781 | [13 empty] | 25
2013-11-13 | 1371 | [13 empty] | 7
2013-11-14 | 1133 | [13 empty] | 3
2013-11-15 | 1180 | [13 empty] | 8
2013-11-16 | 1102 | [13 empty] | 4
2013-11-17 | 1298 | [13 empty] | 3
2013-11-18 | 1148 | [13 empty] | 5
2013-11-19 | 1116 | 0.38 | 2 | 7.2 | 1 | 4 | 2 | 4.9 | 0.12 | 2.382 | 5.8359 | 2.382 | 0.14292 | 4.764 | 3
2013-11-20 | 1126 | [13 empty] | 4
2013-11-21 | 1100 | [13 empty] | 0
2013-11-22 | 654 | [13 empty] | 0
2013-11-23 | 1347 | [13 empty] | 0
2013-11-24 | 1363 | [13 empty] | 11
2013-11-25 | 1298 | [13 empty] | 16
2013-11-26 | 1059 | [13 empty] | 0
2013-11-27 | 1067 | [13 empty] | 0
2013-11-28 | 656 | [13 empty] | 0
2013-11-29 | 1314 | [13 empty] | 0
2013-11-30 | 1102 | [13 empty] | 0
2013-12-01 | 1572 | [13 empty] | 26
2013-12-02 | 1167 | [13 empty] | 13
2013-12-03 | 1204 | 0.48 | 2 | 7.6 | 1 | 5 | 2 | 5.2 | 0.13 | 2.4 | 6.24 | 2.4 | 0.156 | 6 | 0
2013-12-04 | 1131 | [13 empty] | 0
2013-12-05 | 1116 | [13 empty] | 0
2013-12-06 | 1135 | [13 empty] | 0
2013-12-07 | 704 | [13 empty] | 0
2013-12-08 | 1590 | [13 empty] | 0
2013-12-09 | 1110 | [13 empty] | 0
2013-12-10 | 1146 | [13 empty] | 0
2013-12-11 | 1078 | [13 empty] | 0
2013-12-12 | 1143 | [13 empty] | 1
2013-12-13 | 1079 | [13 empty] | 8
2013-12-14 | 1102 | [13 empty] | 0
2013-12-15 | 1308 | [13 empty] | 0
2013-12-16 | 1134 | [13 empty] | 0
2013-12-17 | 1114 | 0.3 | 2 | 7.1 | 495 | 3 | 2 | 4.8 | 0.1 | 2.35 | 5.64 | 2.35 | 0.1175 | 3.525 | 0
2013-12-18 | 1114 | [13 empty] | 0
2013-12-19 | 966 | [13 empty] | 0
2013-12-20 | 1076 | [13 empty] | 0
2013-12-21 | 1178 | [13 empty] | 0
2013-12-22 | 1288 | [13 empty] | 0
2013-12-23 | 1275 | [13 empty] | 0
2013-12-24 | 1159 | [13 empty] | 0
2013-12-25 | 1244 | [13 empty] | 0
2013-12-26 | 1340 | [13 empty] | 0
2013-12-27 | 1152 | [13 empty] | 0
2013-12-28 | 1516 | [13 empty] | 0
2013-12-29 | 1416 | [13 empty] | 0
2013-12-30 | 1142 | [13 empty] | 0
2013-12-31 | 1544 | 1.9 | 2 | 7.1 | 18 | 6 | 2 | 10 | 0.19 | 3.014 | 15.07 | 3.014 | 0.28633 | 9.042 | 6
2014-01-01 | 1587 | [13 empty] | 0
2014-01-02 | 1226 | [13 empty] | 0
2014-01-03 | 1479 | [13 empty] | 0
2014-01-04 | 1557 | [13 empty] | 0
2014-01-05 | 1306 | [13 empty] | 0
2014-01-06 | 1523 | [13 empty] | 0
2014-01-07 | 1109 | [13 empty] | 0
2014-01-08 | 1285 | [13 empty] | 0
2014-01-09 | 1675 | [13 empty] | 0
2014-01-10 | 1148 | [13 empty] | 11
2014-01-11 | 1294 | [13 empty] | 2
2014-01-12 | 1369 | [13 empty] | 0
2014-01-13 | 1401 | [13 empty] | 0
2014-01-14 | 1002 | 0.82 | 2 | 7.1 | 10 | 4 | 2 | 7.8 | 0.17 | 2.6 | 10.14 | 2.6 | 0.221 | 5.2 | 0
2014-01-15 | 1561 | [13 empty] | 3
2014-01-16 | 1265 | [13 empty] | 0
2014-01-17 | 1214 | [13 empty] | 0
2014-01-18 | 1189 | [13 empty] | 0
2014-01-19 | 925 | [13 empty] | 0
2014-01-20 | 1517 | [13 empty] | 0
2014-01-21 | 928 | [13 empty] | 0
2014-01-22 | 1193 | [13 empty] | 10
2014-01-23 | 1302 | [13 empty] | 0
2014-01-24 | 1011 | [13 empty] | 5
2014-01-25 | 1250 | [13 empty] | 14
2014-01-26 | 1091 | [13 empty] | 0
2014-01-27 | 1534 | [13 empty] | 3
2014-01-28 | 1200 | 0.83 | 2 | 7.7 | 1 | 1 | 2 | 6.3 | 0.12 | 2.524 | 7.9506 | 2.524 | 0.15144 | 1.262 | 1
2014-01-29 | 1048 | [13 empty] | 0
2014-01-30 | 868 | [13 empty] | 0
2014-01-31 | 1024 | [13 empty] | 0
2014-02-01 | 1025 | [13 empty] | 0
2014-02-02 | 902 | [13 empty] | 0
2014-02-03 | 1018 | [13 empty] | 0
2014-02-04 | 1140 | [13 empty] | 0
2014-02-05 | 1162 | [13 empty] | 0
2014-02-06 | 877 | [13 empty] | 0
2014-02-07 | 1009 | [13 empty] | 12
2014-02-08 | 1041 | [13 empty] | 7
2014-02-09 | 915 | [13 empty] | 0
2014-02-10 | 1308 | [13 empty] | 0
2014-02-11 | 1025 | 0.09 | 2 | 7.2 | 6 | 1 | 2 | 5 | 0.05 | 2.018 | 5.045 | 2.018 | 0.05045 | 1.009 | 0
2014-02-12 | 724 | [13 empty] | 0
2014-02-13 | 1136 | [13 empty] | 0
2014-02-14 | 950 | [13 empty] | 0
2014-02-15 | 1004 | [13 empty] | 0
2014-02-16 | 900 | [13 empty] | 0
2014-02-17 | 1161 | [13 empty] | 0
2014-02-18 | 980 | [13 empty] | 0
2014-02-19 | 977 | [13 empty] | 0
2014-02-20 | 1035 | [13 empty] | 0
2014-02-21 | 972 | [13 empty] | 0
2014-02-22 | 853 | [13 empty] | 0
2014-02-23 | 1267 | [13 empty] | 1
2014-02-24 | 810 | [13 empty] | 0
2014-02-25 | 1010 | 0.16 | 2 | 7.8 | 1 | 1 | 2 | 6.4 | 0.08 | 1.986 | 6.3552 | 1.986 | 0.07944 | 0.993 | 4
2014-02-26 | 1018 | [13 empty] | 0
2014-02-27 | 976 | [13 empty] | 7
2014-02-28 | 853 | [13 empty] | 0
2014-03-01 | 1241 | [13 empty] | 0
2014-03-02 | 729 | [13 empty] | 6
2014-03-03 | 1287 | [13 empty] | 0
2014-03-04 | 997 | [13 empty] | 11
2014-03-05 | 777 | [13 empty] | 0
2014-03-06 | 910 | [13 empty] | 0
2014-03-07 | 941 | [13 empty] | 0
2014-03-08 | 962 | [13 empty] | 0
2014-03-09 | 858 | [13 empty] | 0
2014-03-10 | 1091 | [13 empty] | 0
2014-03-11 | 955 | 0.4 | 2 | 7.3 | 1 | 3 | 2 | 4.7 | 0.15 | 1.938 | 4.5543 | 1.938 | 0.14535 | 2.907 | 0
2014-03-12 | 1033 | [13 empty] | 2
2014-03-13 | 845 | [13 empty] | 14
2014-03-14 | 1094 | [13 empty] | 1
2014-03-15 | 985 | [13 empty] | 1
2014-03-16 | 911 | [13 empty] | 0
2014-03-17 | 1235 | [13 empty] | 0
2014-03-18 | 1028 | [13 empty] | 0
2014-03-19 | 951 | [13 empty] | 0
2014-03-20 | 1165 | [13 empty] | 0
2014-03-21 | 1220 | [13 empty] | 48
2014-03-22 | 1497 | [13 empty] | 32
2014-03-23 | 1195 | [13 empty] | 1
2014-03-24 | 1091 | [13 empty] | 0
2014-03-25 | 1167 | 0.07 | 2 | 7.4 | 90 | 4 | 2 | 5.3 | 0.07 | 2.242 | 5.9413 | 2.242 | 0.07847 | 4.484 | 0
2014-03-26 | 951 | [13 empty] | 9
2014-03-27 | 1087 | [13 empty] | 3
2014-03-28 | 1300 | [13 empty] | 0
2014-03-29 | 2111 | [13 empty] | 104
2014-03-30 | 1736 | [13 empty] | 12
2014-03-31 | 135 | 4.6 | 2 | 7.4 | 6200 | 22 | 7 | 7.8 | 0.78 | 10.395 | 11.583 | 2.97 | 1.1583 | 32.67 | 1
2014-04-01 | 1735 | 2.3 | 2 | 7.4 | 22 | 7 | 2 | 4.5 | 0.38 | 3.314 | 7.4565 | 3.314 | 0.62966 | 11.599 | 0
2014-04-02 | 1426 | [13 empty] | 0
2014-04-03 | 1579 | [13 empty] | 0
2014-04-04 | 1259 | [13 empty] | 0
2014-04-05 | 1469 | [13 empty] | 0
2014-04-06 | 1117 | [13 empty] | 0
2014-04-07 | 1686 | [13 empty] | 38
2014-04-08 | 1810 | 0.56 | 2 | 7.1 | 1 | 4 | 4 | 5.6 | 0.2 | 6.656 | 9.3184 | 3.328 | 0.3328 | 6.656 | 2
2014-04-09 | 1396 | [13 empty] | 2
2014-04-10 | 1541 | [13 empty] | 0
2014-04-11 | 1248 | [13 empty] | 0
2014-04-12 | 1394 | [13 empty] | 0
2014-04-13 | 1181 | [13 empty] | 0
2014-04-14 | 1296 | [13 empty] | 0
2014-04-15 | 2177 | [13 empty] | 31
2014-04-16 | 1444 | [13 empty] | 41
2014-04-17 | 1801 | [13 empty] | 0
2014-04-18 | 1742 | [13 empty] | 0
2014-04-19 | 1906 | [13 empty] | 0
2014-04-20 | 1465 | [13 empty] | 0
2014-04-21 | 1723 | [13 empty] | 0
2014-04-22 | 1648 | 0.62 | 2 | 7.2 | 1 | 6 | 2 | 7.8 | 0.23 | 3.254 | 12.6906 | 3.254 | 0.37421 | 9.762 | 0
2014-04-23 | 1333 | [13 empty] | 0
2014-04-24 | 1421 | [13 empty] | 0
2014-04-25 | 1352 | [13 empty] | 0
2014-04-26 | 1373 | [13 empty] | 0
2014-04-27 | 1340 | [13 empty] | 2
2014-04-28 | 1301 | [13 empty] | 0
2014-04-29 | 2681 | [13 empty] | 69
2014-04-30 | 1573 | [13 empty] | 2
2014-05-01 | 1840 | [13 empty] | 0
2014-05-02 | 1465 | [13 empty] | 0
2014-05-03 | 1956 | [13 empty] | 1
2014-05-04 | 1472 | [13 empty] | 12
2014-05-05 | 1460 | [13 empty] | 0
2014-05-06 | 1551 | 0.52 | 2 | 7.7 | 9 | 7 | 2 | 6.5 | 0.12 | 3.154 | 10.2505 | 3.154 | 0.18924 | 11.039 | 0
2014-05-07 | 1420 | [13 empty] | 0
2014-05-08 | 1151 | [13 empty] | 0
2014-05-09 | 1333 | [13 empty] | 6
2014-05-10 | 1764 | [13 empty] | 7
2014-05-11 | 1051 | [13 empty] | 0
2014-05-12 | 1529 | [13 empty] | 0
2014-05-13 | 1129 | [13 empty] | 0
2014-05-14 | 1273 | [13 empty] | 2
2014-05-15 | 1484 | [13 empty] | 8
2014-05-16 | 1088 | [13 empty] | 0
2014-05-17 | 1526 | [13 empty] | 0
2014-05-18 | 1169 | [13 empty] | 3
2014-05-19 | 1082 | [13 empty] | 0
2014-05-20 | 1535 | 0.34 | 2 | 7.2 | 1 | 1 | 2 | 4.4 | 0.12 | 2.472 | 5.4384 | 2.472 | 0.14832 | 1.236 | 0
2014-05-21 | 1062 | [13 empty] | 0
2014-05-22 | 1032 | [13 empty] | 0
2014-05-23 | 1214 | [13 empty] | 0
2014-05-24 | 1464 | [13 empty] | 0
2014-05-25 | 987 | [13 empty] | 0
2014-05-26 | 1551 | [13 empty] | 0
2014-05-27 | 1177 | [13 empty] | 0
2014-05-28 | 1137 | [13 empty] | 0
2014-05-29 | 1135 | [13 empty] | 0
2014-05-30 | 1161 | [13 empty] | 0
2014-05-31 | 1127 | [13 empty] | 0
MINIMUM | 135 | 0.07 | 2 | 6.6 | 1 | 1 | 2 | 4.1 | 0.05 | 1.938 | 4.5543 | 1.938 | 0.05045 | 0.993 | 0
AVERAGE | 1287.4137 | 0.90071 | 2 | 7.1929 | 247.1786 | 6.2857 | 2.3214 | 6.0679 | 0.20679 | 3.194 | 8.2723 | 2.7049 | 0.30118 | 9.3181 | 2.8027
MAXIMUM | 3177 | 4.6 | 2 | 7.8 | 6200 | 22 | 7 | 10 | 0.78 | 10.395 | 17.355 | 3.9 | 1.1583 | 35.1 | 104
| Sample Count | 28 | [6 empty] | Total | 86.959 | 226.1852 | 73.264 | 8.2848 | 259.67 | 1023

## 14-15
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 14/15
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | SS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| ML/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | -
2014-06-01 | 1128 | [13 empty] | 0
2014-06-02 | 1225 | [13 empty] | 1
2014-06-03 | 1132 | 0.18 | 2 | 7.2 | 6 | 5 | 2 | 5.7 | 0.17 | 2.346 | 6.6861 | 2.346 | 0.19941 | 5.865 | 0
2014-06-04 | 1200 | [13 empty] | 0
2014-06-05 | 1106 | [13 empty] | 0
2014-06-06 | 896 | [13 empty] | 15
2014-06-07 | 1212 | [13 empty] | 2.5
2014-06-08 | 1089 | [13 empty] | 0
2014-06-09 | 1518 | [13 empty] | 0
2014-06-10 | 1200 | [13 empty] | 0
2014-06-11 | 1145 | [13 empty] | 0
2014-06-12 | 1194 | [13 empty] | 3
2014-06-13 | 958 | [13 empty] | 1
2014-06-14 | 1518 | [13 empty] | 0
2014-06-15 | 932 | [13 empty] | 0
2014-06-16 | 1445 | [13 empty] | 0
2014-06-17 | 1070 | 0.41 | 2 | 6.9 | 9 | 2 | 2 | 5.8 | 0.2 | 2.598 | 7.5342 | 2.598 | 0.2598 | 2.598 | 0
2014-06-18 | 1454 | [13 empty] | 0
2014-06-19 | 1194 | [13 empty] | 3.5
2014-06-20 | 1085 | [13 empty] | 0
2014-06-21 | 1055 | [13 empty] | 0
2014-06-22 | 1308 | [13 empty] | 0
2014-06-23 | 1603 | [13 empty] | 0
2014-06-24 | 928 | [13 empty] | 0
2014-06-25 | 1180 | [13 empty] | 0
2014-06-26 | 1402 | [13 empty] | 27.5
2014-06-27 | 1133 | [13 empty] | 4.5
2014-06-28 | 1055 | [13 empty] | 4
2014-06-29 | 1423 | [13 empty] | 1
2014-06-30 | 1091 | [13 empty] | 0
2014-07-01 | 1507 | 0.48 | 2 | 7.2 | 2 | 4 | 2 | 5.2 | 0.13 | 2.738 | 7.1188 | 2.738 | 0.17797 | 5.476 | 0
2014-07-02 | 949 | [13 empty] | 2
2014-07-03 | 1120 | [13 empty] | 0
2014-07-04 | 1454 | [13 empty] | 0
2014-07-05 | 1171 | [13 empty] | 28
2014-07-06 | 1224 | [13 empty] | 3
2014-07-07 | 1206 | [13 empty] | 0
2014-07-08 | 1170 | [13 empty] | 1
2014-07-09 | 1172 | [13 empty] | 9
2014-07-10 | 1110 | [13 empty] | 1
2014-07-11 | 1202 | [13 empty] | 0
2014-07-12 | 1080 | [13 empty] | 14
2014-07-13 | 1339 | [13 empty] | 1
2014-07-14 | 1040 | [13 empty] | 3
2014-07-15 | 846 | 0.89 | 2 | 7.1 | 1 | 2 | 2 | 6 | 0.13 | 2.246 | 6.738 | 2.246 | 0.14599 | 2.246 | 1
2014-07-16 | 990 | [13 empty] | 0
2014-07-17 | 924 | [13 empty] | 5
2014-07-18 | 1086 | [13 empty] | 3
2014-07-19 | 1088 | [13 empty] | 10
2014-07-20 | 1361 | [13 empty] | 0
2014-07-21 | 1055 | [13 empty] | 0
2014-07-22 | 972 | [13 empty] | 0
2014-07-23 | 974 | [13 empty] | 0
2014-07-24 | 1489 | [13 empty] | 0
2014-07-25 | 1205 | [13 empty] | 0
2014-07-26 | 1157 | [13 empty] | 0
2014-07-27 | 1083 | [13 empty] | 28
2014-07-28 | 836 | [13 empty] | 59
2014-07-29 | 1450 | 0.5 | 2 | 7.1 | 1 | 4 | 2 | 4.8 | 0.09 | 2.63 | 6.312 | 2.63 | 0.11835 | 5.26 | 16
2014-07-30 | 1147 | [13 empty] | 0
2014-07-31 | 886 | [13 empty] | 0
2014-08-01 | 1067 | [13 empty] | 0
2014-08-02 | 1188 | [13 empty] | 0
2014-08-03 | 1343 | [13 empty] | 1
2014-08-04 | 898 | [13 empty] | 1
2014-08-05 | 1195 | [13 empty] | 0
2014-08-06 | 1218 | [13 empty] | 1
2014-08-07 | 1226 | [13 empty] | 0
2014-08-08 | 1276 | [13 empty] | 0
2014-08-09 | 1101 | [13 empty] | 0
2014-08-10 | 1015 | [13 empty] | 0
2014-08-11 | 1284 | [13 empty] | 0
2014-08-12 | 1176 | 0.52 | 2 | 8.1 | 11 | 2 | 2 | 4.6 | 0.11 | 2.552 | 5.8696 | 2.552 | 0.14036 | 2.552 | 1
2014-08-13 | 1235 | [13 empty] | 0
2014-08-14 | 1196 | [13 empty] | 0
2014-08-15 | 1013 | [13 empty] | 0
2014-08-16 | 1196 | [13 empty] | 0
2014-08-17 | 1445 | [13 empty] | 0
2014-08-18 | 1755 | [13 empty] | 0
2014-08-19 | 1205 | [13 empty] | 0
2014-08-20 | 1653 | [13 empty] | 7
2014-08-21 | 1143 | [13 empty] | 0
2014-08-22 | 1532 | [13 empty] | 0
2014-08-23 | 1688 | [13 empty] | 15.5
2014-08-24 | 3292 | [13 empty] | 11
2014-08-25 | 2046 | [13 empty] | 25
2014-08-26 | 1944 | 0.23 | 2 | 7.2 | 3 | 4 | 2 | 2.3 | 0.13 | 3.722 | 4.2803 | 3.722 | 0.24193 | 7.444 | 57
2014-08-27 | 1940 | [13 empty] | 1
2014-08-28 | 3574 | [13 empty] | 32
2014-08-29 | 3856 | [13 empty] | 5
2014-08-30 | 2767 | [13 empty] | 0
2014-08-31 | 2118 | [13 empty] | 0
2014-09-01 | 1985 | [13 empty] | 1.5
2014-09-02 | 1865 | [13 empty] | 0
2014-09-03 | 2146 | [13 empty] | 9
2014-09-04 | 1592 | [13 empty] | 9
2014-09-05 | 1650 | [13 empty] | 0
2014-09-06 | 1884 | [13 empty] | 1
2014-09-07 | 1427 | [13 empty] | 0
2014-09-08 | 1781 | [13 empty] | 0
2014-09-09 | 1417 | 0.3 | 2 | 7.2 | 2 | 6 | 2 | 4 | 0.14 | 3.232 | 6.464 | 3.232 | 0.22624 | 9.696 | 0
2014-09-10 | 1702 | [13 empty] | 8
2014-09-11 | 1372 | [13 empty] | 3
2014-09-12 | 1703 | [13 empty] | 1
2014-09-13 | 1563 | [13 empty] | 5
2014-09-14 | 1475 | [13 empty] | 1.5
2014-09-15 | 1596 | [13 empty] | 1
2014-09-16 | 1365 | [13 empty] | 0
2014-09-17 | 1561 | [13 empty] | 0
2014-09-18 | 1228 | [13 empty] | 4
2014-09-19 | 1201 | [13 empty] | 5
2014-09-20 | 1366 | [13 empty] | 41
2014-09-21 | 1587 | [13 empty] | 90
2014-09-22 | 1412 | [13 empty] | 31
2014-09-23 | 1447 | 0.39 | 2 | 6.9 | 5 | 6 | 2 | 5.3 | 0.26 | 2.812 | 7.4518 | 2.812 | 0.36556 | 8.436 | 23
2014-09-24 | 1451 | [13 empty] | 4
2014-09-25 | 1290 | [13 empty] | 2
2014-09-26 | 1649 | [13 empty] | 0
2014-09-27 | 1294 | [13 empty] | 2
2014-09-28 | 1651 | [13 empty] | 0
2014-09-29 | 1192 | [13 empty] | 0
2014-09-30 | 1592 | [13 empty] | 13
2014-10-01 | 1192 | [13 empty] | 3
2014-10-02 | 1878 | [13 empty] | 0
2014-10-03 | 1569 | [13 empty] | 0
2014-10-04 | 1390 | [13 empty] | 0
2014-10-05 | 1554 | [13 empty] | 0
2014-10-06 | 1113 | [13 empty] | 0
2014-10-07 | 1653 | 0.63 | 2 | 7.3 | 7 | 1 | 2 | 8.9 | 0.11 | 2.702 | 12.0239 | 2.702 | 0.14861 | 1.351 | 0
2014-10-08 | 1056 | [13 empty] | 0
2014-10-09 | 1447 | [13 empty] | 0
2014-10-10 | 1189 | [13 empty] | 0
2014-10-11 | 1171 | [13 empty] | 0
2014-10-12 | 994 | [13 empty] | 2
2014-10-13 | 1629 | [13 empty] | 0
2014-10-14 | 1116 | [13 empty] | 2.5
2014-10-15 | 1416 | [13 empty] | 0
2014-10-16 | 1014 | [13 empty] | 1
2014-10-17 | 1388 | [13 empty] | 11
2014-10-18 | 1040 | [13 empty] | 0
2014-10-19 | 1286 | [13 empty] | 0
2014-10-20 | 1198 | [13 empty] | 14
2014-10-21 | 1410 | 0.39 | 2 | 7.2 | 5 | 2 | 2 | 6.5 | 0.08 | 2.272 | 7.384 | 2.272 | 0.09088 | 2.272 | 15
2014-10-22 | 977 | [13 empty] | 1
2014-10-23 | 1387 | [13 empty] | 0
2014-10-24 | 1027 | [13 empty] | 0
2014-10-25 | 1388 | [13 empty] | 20
2014-10-26 | 1049 | [13 empty] | 0
2014-10-27 | 1416 | [13 empty] | 0
2014-10-28 | 1021 | [13 empty] | 0
2014-10-29 | 1289 | [13 empty] | 0
2014-10-30 | 940 | [13 empty] | 2
2014-10-31 | 1304 | [13 empty] | 6
2014-11-01 | 1000 | [13 empty] | 2
2014-11-02 | 1134 | [13 empty] | 12
2014-11-03 | 1137 | [13 empty] | 32
2014-11-04 | 1302 | 0.33 | 2 | 7.5 | 24 | 5 | 2 | 5.5 | 0.15 | 2.198 | 6.0445 | 2.198 | 0.16485 | 5.495 | 0
2014-11-05 | 928 | [13 empty] | 3
2014-11-06 | 1392 | [13 empty] | 0
2014-11-07 | 1101 | [13 empty] | 0
2014-11-08 | 1183 | [13 empty] | 0
2014-11-09 | 1228 | [13 empty] | 0
2014-11-10 | 1416 | [13 empty] | 0
2014-11-11 | 994 | [13 empty] | 0
2014-11-12 | 1294 | [13 empty] | 0
2014-11-13 | 927 | [13 empty] | 0
2014-11-14 | 1293 | [13 empty] | 0
2014-11-15 | 1037 | [13 empty] | 0
2014-11-16 | 1439 | [13 empty] | 0
2014-11-17 | 1021 | [13 empty] | 0
2014-11-18 | 1344 | 0.45 | 2 | 7.5 | 1 | 4 | 2 | 5.7 | 0.14 | 2.238 | 6.3783 | 2.238 | 0.15666 | 4.476 | 6
2014-11-19 | 1109 | [13 empty] | 2
2014-11-20 | 1109 | [13 empty] | 0
2014-11-21 | 2161 | [13 empty] | 0
2014-11-22 | 1529 | [13 empty] | 0
2014-11-23 | 1185 | [13 empty] | 0
2014-11-24 | 1175 | [13 empty] | 0
2014-11-25 | 1019 | [13 empty] | 0
2014-11-26 | 1121 | [13 empty] | 0
2014-11-27 | 970 | [13 empty] | 0
2014-11-28 | 1200 | [13 empty] | 6
2014-11-29 | 1247 | [13 empty] | 31
2014-11-30 | 1043 | [13 empty] | 155
2014-12-01 | 1437 | [13 empty] | 11
2014-12-02 | 1116 | 0.21 | 2 | 7.9 | 1 | 3 | 2 | 4.5 | 0.13 | 2.234 | 5.0265 | 2.234 | 0.14521 | 3.351 | 2
2014-12-03 | 1117 | [13 empty] | 0
2014-12-04 | 854 | [13 empty] | 0
2014-12-05 | 854 | [13 empty] | 0
2014-12-06 | 2497 | [13 empty] | 0
2014-12-07 | 1044 | [13 empty] | 0
2014-12-08 | 1494 | [13 empty] | 0
2014-12-09 | 1306 | [13 empty] | 0
2014-12-10 | 1140 | [13 empty] | 0
2014-12-11 | 1217 | [13 empty] | 0
2014-12-12 | 1271 | [13 empty] | 0
2014-12-13 | 1466 | [13 empty] | 0
2014-12-14 | 980 | [13 empty] | 0
2014-12-15 | 1298 | [13 empty] | 7
2014-12-16 | 1701 | 0.38 | 2 | 8.3 | 1 | 2 | 2 | 5.2 | 0.09 | 2.762 | 7.1812 | 2.762 | 0.12429 | 2.762 | 3
2014-12-17 | 1297 | [13 empty] | 0
2014-12-18 | 1673 | [13 empty] | 0
2014-12-19 | 1244 | [13 empty] | 0
2014-12-20 | 1294 | [13 empty] | 10
2014-12-21 | 1142 | [13 empty] | 0
2014-12-22 | 1346 | [13 empty] | 0
2014-12-23 | 1683 | [13 empty] | 0
2014-12-24 | 1031 | [13 empty] | 0
2014-12-25 | 1301 | [13 empty] | 0
2014-12-26 | 1408 | [13 empty] | 0
2014-12-27 | 1294 | [13 empty] | 0
2014-12-28 | 1896 | [13 empty] | 0
2014-12-29 | 2467 | [13 empty] | 0
2014-12-30 | 2319 | 1.2 | 2 | 7 | 1 | 3 | 2 | 8.2 | 0.09 | 4.452 | 18.2532 | 4.452 | 0.20034 | 6.678 | 0
2014-12-31 | 1668 | [13 empty] | 0
2015-01-01 | 2469 | [13 empty] | 0
2015-01-02 | 1764 | [13 empty] | 0
2015-01-03 | 2273 | [13 empty] | 0
2015-01-04 | 1666 | [13 empty] | 0
2015-01-05 | 1800 | [13 empty] | 1.5
2015-01-06 | 2044 | [13 empty] | 0
2015-01-07 | 1488 | [13 empty] | 0
2015-01-08 | 1988 | [13 empty] | 0
2015-01-09 | 1350 | [13 empty] | 1
2015-01-10 | 1913 | [13 empty] | 1
2015-01-11 | 1476 | [13 empty] | 7
2015-01-12 | 1617 | [13 empty] | 2
2015-01-13 | 1815 | 0.54 | 2 | 7 | 1 | 1 | 2 | 7.5 | 0.09 | 3.372 | 12.645 | 3.372 | 0.15174 | 1.686 | 2
2015-01-14 | 1390 | [13 empty] | 1
2015-01-15 | 1810 | [13 empty] | 3
2015-01-16 | 1352 | [13 empty] | 0
2015-01-17 | 1708 | [13 empty] | 0
2015-01-18 | 1279 | [13 empty] | 0
2015-01-19 | 1678 | [13 empty] | 0
2015-01-20 | 1230 | [13 empty] | 3
2015-01-21 | 2598 | [13 empty] | 0
2015-01-22 | 1692 | [13 empty] | 0
2015-01-23 | 2932 | [13 empty] | 0
2015-01-24 | 3236 | [13 empty] | 1
2015-01-25 | 2204 | [13 empty] | 1
2015-01-26 | 2162 | [13 empty] | 1
2015-01-27 | 1599 | 0.52 | 2 | 7 | 136 | 2 | 2 | 4.4 | 0.06 | 3.996 | 8.7912 | 3.996 | 0.11988 | 3.996 | 0
2015-01-28 | 1767 | [13 empty] | 0
2015-01-29 | 2376 | [13 empty] | 0
2015-01-30 | 2023 | [13 empty] | 4
2015-01-31 | 1477 | [13 empty] | 0
2015-02-01 | 1844 | [13 empty] | 0
2015-02-02 | 1649 | [13 empty] | 0
2015-02-03 | 1481 | [13 empty] | 0
2015-02-04 | 2186 | [13 empty] | 0
2015-02-05 | 1683 | [13 empty] | 0
2015-02-06 | 1107 | [13 empty] | 1
2015-02-07 | 1707 | [13 empty] | 5
2015-02-08 | 1565 | [13 empty] | 0
2015-02-09 | 1560 | [13 empty] | 1
2015-02-10 | 1346 | 0.29 | 2 | 7 | 2 | 3 | 2 | 3.4 | 0.13 | 3.062 | 5.2054 | 3.062 | 0.19903 | 4.593 | 0
2015-02-11 | 1644 | [13 empty] | 0
2015-02-12 | 1214 | [13 empty] | 0
2015-02-13 | 1688 | [13 empty] | 0
2015-02-14 | 1317 | [13 empty] | 0
2015-02-15 | 1546 | [13 empty] | 0
2015-02-16 | 1775 | [13 empty] | 0
2015-02-17 | 1412 | [13 empty] | 0
2015-02-18 | 1331 | [13 empty] | 1
2015-02-19 | 1161 | [13 empty] | 1
2015-02-20 | 1288 | [13 empty] | 0
2015-02-21 | 3457 | [13 empty] | 0
2015-02-22 | 3370 | [13 empty] | 9.5
2015-02-23 | 3595 | [13 empty] | 0
2015-02-24 | 2798 | 0.32 | 2 | 8.1 | 1 | 2 | 2 | 2.5 | 0.12 | 5.43 | 6.7875 | 5.43 | 0.3258 | 5.43 | 0
2015-02-25 | 1926 | [13 empty] | 0
2015-02-26 | 1913 | [13 empty] | 0
2015-02-27 | 2218 | [13 empty] | 0
2015-02-28 | 1716 | [13 empty] | 0
2015-03-01 | 1982 | [13 empty] | 0
2015-03-02 | 1152 | [13 empty] | 0
2015-03-03 | 1637 | [13 empty] | 0
2015-03-04 | 1540 | [13 empty] | 0
2015-03-05 | 1754 | [13 empty] | 0
2015-03-06 | 1739 | [13 empty] | 0
2015-03-07 | 1089 | [13 empty] | 0
2015-03-08 | 1482 | [13 empty] | 0
2015-03-09 | 1520 | [13 empty] | 0
2015-03-10 | 1499 | 0.28 | 2 | 6.9 | 2 | 4 | 2 | 4.2 | 0.14 | 2.962 | 6.2202 | 2.962 | 0.20734 | 5.924 | 0
2015-03-11 | 1481 | [13 empty] | 0
2015-03-12 | 1410 | [13 empty] | 0
2015-03-13 | 1627 | [13 empty] | 0
2015-03-14 | 1250 | [13 empty] | 0
2015-03-15 | 1821 | [13 empty] | 0
2015-03-16 | 1091 | [13 empty] | 0.5
2015-03-17 | 1757 | [13 empty] | 1
2015-03-18 | 1084 | [13 empty] | 0
2015-03-19 | 1345 | [13 empty] | 0
2015-03-20 | 1202 | [13 empty] | 1
2015-03-21 | 1683 | [13 empty] | 1
2015-03-22 | 1289 | [13 empty] | 0
2015-03-23 | 1503 | [13 empty] | 0
2015-03-24 | 1809 | 0.51 | 2 | 7.6 | 1 | 6 | 2 | 5.6 | 0.13 | 3.442 | 9.6376 | 3.442 | 0.22373 | 10.326 | 0
2015-03-25 | 1591 | [13 empty] | 28
2015-03-26 | 1496 | [13 empty] | 0
2015-03-27 | 1496 | [13 empty] | 0
2015-03-28 | 3089 | [13 empty] | 4
2015-03-29 | 1417 | [13 empty] | 0
2015-03-30 | 1021 | [13 empty] | 0
2015-03-31 | 1512 | [13 empty] | 0
2015-04-01 | 1262 | [13 empty] | 0
2015-04-02 | 1508 | [13 empty] | 0
2015-04-03 | 1431 | [13 empty] | 6
2015-04-04 | 1975 | [13 empty] | 1
2015-04-05 | 2010 | [13 empty] | 0
2015-04-06 | 2927 | [13 empty] | 0
2015-04-07 | 2134 | 2.4 | 2 | 6.9 | 1 | 3 | 2 | 6.8 | 0.22 | 4.508 | 15.3272 | 4.508 | 0.49588 | 6.762 | 0
2015-04-08 | 1810 | [13 empty] | 2
2015-04-09 | 1913 | [13 empty] | 0
2015-04-10 | 1639 | [13 empty] | 0
2015-04-11 | 1168 | [13 empty] | 0
2015-04-12 | 1516 | [13 empty] | 0
2015-04-13 | 1684 | [13 empty] | 0
2015-04-14 | 1354 | [13 empty] | 0
2015-04-15 | 1620 | [13 empty] | 0
2015-04-16 | 1466 | [13 empty] | 0
2015-04-17 | 1395 | [13 empty] | 13
2015-04-18 | 1189 | [13 empty] | 13
2015-04-19 | 1429 | [13 empty] | 5
2015-04-20 | 1639 | [13 empty] | 1
2015-04-21 | 1275 | 0.24 | 2 | 7.7 | 1 | 3 | 2 | 4.8 | 0.18 | 2.61 | 6.264 | 2.61 | 0.2349 | 3.915 | 5
2015-04-22 | 985 | [13 empty] | 0
2015-04-23 | 1495 | [13 empty] | 0
2015-04-24 | 1259 | [13 empty] | 1
2015-04-25 | 1269 | [13 empty] | 0
2015-04-26 | 1483 | [13 empty] | 0
2015-04-27 | 989 | [13 empty] | 1
2015-04-28 | 1454 | [13 empty] | 0
2015-04-29 | 1239 | [13 empty] | 0
2015-04-30 | 1693 | [13 empty] | 6
2015-05-01 | 3265 | [13 empty] | 0
2015-05-02 | 3844 | [13 empty] | 0
2015-05-03 | 3864 | [13 empty] | 0
2015-05-04 | 3569 | [13 empty] | 0
2015-05-05 | 2996 | 0.57 | 2 | 6.7 | 11 | 37 | 15 | 6.1 | 1.3 | 45.24 | 18.3976 | 6.032 | 3.9208 | 111.592 | 0
2015-05-06 | 2570 | [13 empty] | 0
2015-05-07 | 2402 | [13 empty] | 0
2015-05-08 | 1958 | [13 empty] | 0
2015-05-09 | 2061 | [13 empty] | 2
2015-05-10 | 2090 | [13 empty] | 0
2015-05-11 | 1950 | [13 empty] | 0
2015-05-12 | 2124 | [13 empty] | 0
2015-05-13 | 1768 | [13 empty] | 2
2015-05-14 | 1803 | [13 empty] | 3
2015-05-15 | 1618 | [13 empty] | 5
2015-05-16 | 1750 | [13 empty] | 0
2015-05-17 | 1627 | [13 empty] | 0
2015-05-18 | 2017 | [13 empty] | 0
2015-05-19 | 1915 | 0.51 | 2 | 6.8 | 1 | 4 | 2 | 4 | 0.07 | 3.532 | 7.064 | 3.532 | 0.12362 | 7.064 | 0
2015-05-20 | 1630 | [13 empty] | 0
2015-05-21 | 1544 | [13 empty] | 0
2015-05-22 | 2105 | [13 empty] | 0
2015-05-23 | 1458 | [13 empty] | 19
2015-05-24 | 1962 | [13 empty] | 0
2015-05-25 | 1315 | [13 empty] | 0
2015-05-26 | 1627 | [13 empty] | 0
2015-05-27 | 1617 | [13 empty] | 45
2015-05-28 | 1775 | [13 empty] | 10
2015-05-29 | 1502 | [13 empty] | 14
2015-05-30 | 1375 | [13 empty] | 0
2015-05-31 | 1679 | [13 empty] | 0
MINIMUM | 836 | 0.18 | 2 | 6.7 | 1 | 1 | 2 | 2.3 | 0.06 | 2.198 | 4.2803 | 2.198 | 0.09088 | 1.351 | 0
AVERAGE | 1522.263 | 0.52577 | 2 | 7.2808 | 9.1154 | 4.6154 | 2.5 | 5.2885 | 0.17654 | 4.688 | 8.3495 | 3.18 | 0.34266 | 9.1248 | 3.4397
MAXIMUM | 3864 | 2.4 | 2 | 8.3 | 136 | 37 | 15 | 8.9 | 1.3 | 45.24 | 18.3976 | 6.032 | 3.9208 | 111.592 | 155
| Sample Count | 26 | [6 empty] | Total | 121.888 | 217.0861 | 82.68 | 8.9092 | 237.246 | 1255.5

## 15-16
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 15/16
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Date analysis results obtained | Date Published
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | SS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | -
2015-06-01 | 1588 | [13 empty] | 0
2015-06-02 | 1250 | 0.26 | 1 | 6.8 | 2 | 2 | 2 | 4.2 | 0.1 | 3.042 | 6.3882 | 1.521 | 0.1521 | 3.042 | 0 | 2015-06-12 | 2015-06-26
2015-06-03 | 1519 | [13 empty] | 0
2015-06-04 | 1627 | [13 empty] | 0
2015-06-05 | 1173 | [13 empty] | 0
2015-06-06 | 1413 | [13 empty] | 0
2015-06-07 | 1453 | [13 empty] | 2
2015-06-08 | 1663 | [13 empty] | 4
2015-06-09 | 1508 | [13 empty] | 0
2015-06-10 | 1545 | [13 empty] | 0
2015-06-11 | 1407 | [13 empty] | 0
2015-06-12 | 1251 | [13 empty] | 11
2015-06-13 | 1385 | [13 empty] | 2
2015-06-14 | 1498 | [13 empty] | 3
2015-06-15 | 1227 | [13 empty] | 0
2015-06-16 | 1462 | 0.42 | 1 | 7.1 | 1 | 1 | 2 | 4.1 | 0.09 | 2.908 | 5.9614 | 1.454 | 0.13086 | 1.454 | 0 | 2015-06-29 | 2015-07-13
2015-06-17 | 1321 | [13 empty] | 2
2015-06-18 | 1454 | [13 empty] | 6
2015-06-19 | 1436 | [13 empty] | 0
2015-06-20 | 1474 | [13 empty] | 0
2015-06-21 | 1614 | [13 empty] | 0
2015-06-22 | 1170 | [13 empty] | 1
2015-06-23 | 1559 | [13 empty] | 4
2015-06-24 | 1453 | [13 empty] | 1
2015-06-25 | 1045 | [13 empty] | 0
2015-06-26 | 1679 | [13 empty] | 3
2015-06-27 | 823 | [13 empty] | 2
2015-06-28 | 1862 | [13 empty] | 12
2015-06-29 | 1494 | [13 empty] | 0
2015-06-30 | 1400 | 0.57 | 1 | 6.9 | 6 | 1 | 2 | 6.8 | 0.05 | 3.04 | 10.336 | 1.52 | 0.076 | 1.52 | 0 | 2015-07-13 | 2015-07-13
2015-07-01 | 1251 | [13 empty] | 5
2015-07-02 | 1810 | [13 empty] | 0
2015-07-03 | 1622 | [13 empty] | 0
2015-07-04 | 1434 | [13 empty] | 0
2015-07-05 | 1529 | [13 empty] | 0
2015-07-06 | 1658 | [13 empty] | 0
2015-07-07 | 1246 | [13 empty] | 0
2015-07-08 | 1464 | [13 empty] | 0
2015-07-09 | 1425 | [13 empty] | 2
2015-07-10 | 1451 | [13 empty] | 24
2015-07-11 | 1424 | [13 empty] | 7
2015-07-12 | 1586 | [13 empty] | 0
2015-07-13 | 1748 | [13 empty] | 0
2015-07-14 | 1367 | 0.33 | 1 | 7 | 190 | 1 | 2 | 5.7 | 0.06 | 2.884 | 8.2194 | 1.442 | 0.08652 | 1.442 | 0 | 2015-07-20 | 2015-08-03
2015-07-15 | 987 | [13 empty] | 0
2015-07-16 | 1624 | [13 empty] | 0
2015-07-17 | 1293 | [13 empty] | 0
2015-07-18 | 945 | [13 empty] | 0
2015-07-19 | 1586 | [13 empty] | 0
2015-07-20 | 1407 | [13 empty] | 0
2015-07-21 | 994 | [13 empty] | 12
2015-07-22 | 1618 | [13 empty] | 2
2015-07-23 | 1252 | [13 empty] | 0
2015-07-24 | 1191 | [13 empty] | 2
2015-07-25 | 1503 | [13 empty] | 3
2015-07-26 | 1278 | [13 empty] | 6
2015-07-27 | 1585 | [13 empty] | 0
2015-07-28 | 1013 | 0.58 | 1 | 7.2 | 1 | 3 | 2 | 5.3 | 0.13 | 2.778 | 7.3617 | 1.389 | 0.18057 | 4.167 | 0 | 2015-08-06 | 2015-08-20
2015-07-29 | 1294 | [13 empty] | 0
2015-07-30 | 1502 | [13 empty] | 0
2015-07-31 | 1070 | [13 empty] | 0
2015-08-01 | 1526 | [13 empty] | 0
2015-08-02 | 1162 | [13 empty] | 0
2015-08-03 | 1674 | [13 empty] | 0
2015-08-04 | 1317 | [13 empty] | 0
2015-08-05 | 1209 | [13 empty] | 0
2015-08-06 | 1291 | [13 empty] | 0
2015-08-07 | 642 | [13 empty] | 0
2015-08-08 | 1691 | [13 empty] | 0
2015-08-09 | 1139 | [13 empty] | 0
2015-08-10 | 1241 | [13 empty] | 0
2015-08-11 | 1262 | 0.52 | 1 | 7.1 | 2 | 3 | 2 | 6.3 | 0.17 | 2.644 | 8.3286 | 1.322 | 0.22474 | 3.966 | 0 | 2015-08-19 | 2015-08-20
2015-08-12 | 1242 | [13 empty] | 0
2015-08-13 | 1562 | [13 empty] | 0
2015-08-14 | 1064 | [13 empty] | 0
2015-08-15 | 1396 | [13 empty] | 0
2015-08-16 | 1229 | [13 empty] | 0
2015-08-17 | 1128 | [13 empty] | 3
2015-08-18 | 1352 | [13 empty] | 1
2015-08-19 | 965 | [13 empty] | 0
2015-08-20 | 1179 | [13 empty] | 0
2015-08-21 | 1249 | [13 empty] | 10
2015-08-22 | 1233 | [13 empty] | 6
2015-08-23 | 1405 | [13 empty] | 1
2015-08-24 | 1244 | [13 empty] | 0
2015-08-25 | 1070 | 1.4 | 1 | 7.1 | 3 | 11 | 4 | 3.8 | 0.45 | 5.364 | 5.0958 | 1.341 | 0.60345 | 14.751 | 0 | 2015-09-02 | 2015-09-16
2015-08-26 | 1434 | [13 empty] | 30
2015-08-27 | 1401 | [13 empty] | 0
2015-08-28 | 1173 | [13 empty] | 0
2015-08-29 | 1307 | [13 empty] | 6
2015-08-30 | 977 | [13 empty] | 0
2015-08-31 | 1561 | [13 empty] | 0
2015-09-01 | 1015 | [13 empty] | 0
2015-09-02 | 1614 | [13 empty] | 0
2015-09-03 | 1200 | [13 empty] | 0
2015-09-04 | 1214 | [13 empty] | 4
2015-09-05 | 1155 | [13 empty] | 0
2015-09-06 | 1154 | [13 empty] | 0
2015-09-07 | 1334 | [13 empty] | 0
2015-09-08 | 1154 | 0.48 | 1 | 7.2 | 2 | 2 | 2 | 7 | 0.15 | 2.66 | 9.31 | 1.33 | 0.1995 | 2.66 | 0 | 2015-09-15 | 2015-09-16
2015-09-09 | 1407 | [13 empty] | 18
2015-09-10 | 1176 | [13 empty] | 0
2015-09-11 | 896 | [13 empty] | 0
2015-09-12 | 1381 | [13 empty] | 0
2015-09-13 | 1408 | [13 empty] | 0
2015-09-14 | 732 | [13 empty] | 0
2015-09-15 | 1519 | [13 empty] | 0
2015-09-16 | 1146 | [13 empty] | 0
2015-09-17 | 1343 | [13 empty] | 0
2015-09-18 | 1179 | [13 empty] | 2
2015-09-19 | 1133 | [13 empty] | 25
2015-09-20 | 1650 | [13 empty] | 6
2015-09-21 | 1216 | [13 empty] | 4
2015-09-22 | 1716 | 0.4 | 1 | 7.3 | 2 | 5 | 2 | 6.8 | 0.17 | 2.836 | 9.6424 | 1.418 | 0.24106 | 7.09 | 0 | 2015-09-29 | 2015-10-13
2015-09-23 | 990 | [13 empty] | 0
2015-09-24 | 1370 | [13 empty] | 8
2015-09-25 | 959 | [13 empty] | 0
2015-09-26 | 1645 | [13 empty] | 0
2015-09-27 | 1799 | [13 empty] | 4
2015-09-28 | 1298 | [13 empty] | 19
2015-09-29 | 1385 | [13 empty] | 3
2015-09-30 | 1609 | [13 empty] | 0
2015-10-01 | 1030 | [13 empty] | 0
2015-10-02 | 1574 | [13 empty] | 0
2015-10-03 | 1144 | [13 empty] | 0
2015-10-04 | 1348 | [13 empty] | 0
2015-10-05 | 1343 | [13 empty] | 0
2015-10-06 | 1655 | 0.49 | 1 | 7.1 | 33 | 6 | 3 | 6 | 0.21 | 3.771 | 7.542 | 1.257 | 0.26397 | 7.542 | 0 | 2015-10-12 | 2015-10-13
2015-10-07 | 733 | [13 empty] | 0
2015-10-08 | 1499 | [13 empty] | 0
2015-10-09 | 1116 | [13 empty] | 0
2015-10-10 | 1112 | [13 empty] | 0
2015-10-11 | 1349 | [13 empty] | 0
2015-10-12 | 1194 | [13 empty] | 0
2015-10-13 | 1006 | [13 empty] | 0
2015-10-14 | 1165 | [13 empty] | 0
2015-10-15 | 1143 | [13 empty] | 4
2015-10-16 | 1265 | [13 empty] | 0
2015-10-17 | 1181 | [13 empty] | 0
2015-10-18 | 1338 | [13 empty] | 0
2015-10-19 | 1098 | [13 empty] | 0
2015-10-20 | 1110 | 0.47 | 1 | 7.8 | 6 | 7 | 2 | 6.4 | 0.21 | 2.19 | 7.008 | 1.095 | 0.22995 | 7.665 | 0 | 2015-10-27 | 2015-11-06
2015-10-21 | 1035 | [13 empty] | 0
2015-10-22 | 430 | [13 empty] | 0
2015-10-23 | 1737 | [13 empty] | 0
2015-10-24 | 1227 | [13 empty] | 2
2015-10-25 | 1031 | [13 empty] | 0
2015-10-26 | 1274 | [13 empty] | 0
2015-10-27 | 898 | [13 empty] | 0
2015-10-28 | 651 | [13 empty] | 5
2015-10-29 | 1550 | 0.31 | 1 | 6.7 | 7 | 12 | 3 | 5.6 | 0.36 | 3.186 | 5.9472 | 1.062 | 0.38232 | 12.744 | 2 | 2015-11-11 | 2015-11-25
2015-10-30 | 700 | [13 empty] | 2
2015-10-31 | 830 | [13 empty] | 0
2015-11-01 | 1718 | [13 empty] | 0
2015-11-02 | 830 | [13 empty] | 0
2015-11-03 | 864 | 0.34 | 1 | 7.2 | 84 | 1 | 2 | 4 | 0.08 | 2.152 | 4.304 | 1.076 | 0.08608 | 1.076 | 0 | 2015-11-11 | 2015-11-25
2015-11-04 | 1582 | [13 empty] | 14
2015-11-05 | 718 | [13 empty] | 6
2015-11-06 | 1263 | [13 empty] | 12
2015-11-07 | 891 | [13 empty] | 9
2015-11-08 | 1646 | [13 empty] | 0
2015-11-09 | 1389 | [13 empty] | 3
2015-11-10 | 1330 | [13 empty] | 22
2015-11-11 | 1074 | [13 empty] | 0
2015-11-12 | 1017 | [13 empty] | 0
2015-11-13 | 1310 | [13 empty] | 0
2015-11-14 | 1387 | [13 empty] | 0
2015-11-15 | 1350 | [13 empty] | 23
2015-11-16 | 1337 | [13 empty] | 10
2015-11-17 | 1095 | 0.46 | 1 | 6.7 | 10 | 4 | 2 | 3.5 | 0.13 | 2.638 | 4.6165 | 1.319 | 0.17147 | 5.276 | 10 | 2015-11-24 | 2015-12-08
2015-11-18 | 1347 | [13 empty] | 2
2015-11-19 | 912 | [13 empty] | 0
2015-11-20 | 1554 | [13 empty] | 0
2015-11-21 | 1311 | [13 empty] | 0
2015-11-22 | 1267 | [13 empty] | 0
2015-11-23 | 1335 | [13 empty] | 0
2015-11-24 | 861 | [13 empty] | 31
2015-11-25 | 1740 | [13 empty] | 0
2015-11-26 | 1140 | [13 empty] | 0
2015-11-27 | 997 | [13 empty] | 0
2015-11-28 | 1257 | [13 empty] | 0
2015-11-29 | 1295 | [13 empty] | 2
2015-11-30 | 1577 | [13 empty] | 31
2015-12-01 | 1859 | 1.7 | 1 | 7.2 | 1 | 5 | 3 | 4.6 | 0.1 | 4.704 | 7.2128 | 1.568 | 0.1568 | 7.84 | 0 | 2015-12-15 | 2015-12-29
2015-12-02 | 1134 | [13 empty] | 1
2015-12-03 | 1417 | [13 empty] | 26
2015-12-04 | 1590 | [13 empty] | 0
2015-12-05 | 1233 | [13 empty] | 3
2015-12-06 | 1267 | [13 empty] | 0
2015-12-07 | 1588 | [13 empty] | 0
2015-12-08 | 1146 | [13 empty] | 0
2015-12-09 | 1313 | [13 empty] | 0
2015-12-10 | 815 | [13 empty] | 10
2015-12-11 | 1395 | [13 empty] | 0
2015-12-12 | 945 | [13 empty] | 0
2015-12-13 | 1986 | [13 empty] | 2
2015-12-14 | 1413 | [13 empty] | 0
2015-12-15 | 1424 | 0.22 | 1 | 8.5 | 1 | 2 | 2 | 2.7 | 0.09 | 2.41 | 3.2535 | 1.205 | 0.10845 | 2.41 | 0 | 2015-12-21 | 2015-12-29
2015-12-16 | 1200 | [13 empty] | 1
2015-12-17 | 1198 | [13 empty] | 20
2015-12-18 | 1646 | [13 empty] | 11
2015-12-19 | 1356 | [13 empty] | 0
2015-12-20 | 1311 | [13 empty] | 0
2015-12-21 | 1224 | [13 empty] | 0
2015-12-22 | 1677 | [13 empty] | 0
2015-12-23 | 1308 | [13 empty] | 0
2015-12-24 | 1324 | [13 empty] | 0
2015-12-25 | 770 | [13 empty] | 0
2015-12-26 | 2416 | [13 empty] | 0
2015-12-27 | 1524 | [13 empty] | 4
2015-12-28 | 1696 | [13 empty] | 2
2015-12-29 | 2001 | [13 empty] | 1
2015-12-30 | 1220 | [13 empty] | 2
2015-12-31 | 1955 | [13 empty] | 0
2016-01-01 | 1286 | [13 empty] | 0
2016-01-02 | 1241 | [13 empty] | 0
2016-01-03 | 1456 | [13 empty] | 0
2016-01-04 | 2007 | [13 empty] | 0
2016-01-05 | 1770 | 1.8 | 1 | 7 | 1 | 6 | 2 | 5.7 | 0.14 | 3.336 | 9.5076 | 1.668 | 0.23352 | 10.008 | 10 | 2016-01-14 | 2016-01-28
2016-01-06 | 1154 | [13 empty] | 19
2016-01-07 | 2326 | [13 empty] | 14
2016-01-08 | 1339 | [13 empty] | 0
2016-01-09 | 1853 | [13 empty] | 0
2016-01-10 | 1570 | [13 empty] | 0
2016-01-11 | 1560 | [13 empty] | 0
2016-01-12 | 1551 | [13 empty] | 0
2016-01-13 | 1253 | [13 empty] | 0
2016-01-14 | 1663 | [13 empty] | 0
2016-01-15 | 1251 | [13 empty] | 0
2016-01-16 | 1213 | [13 empty] | 0
2016-01-17 | 1403 | [13 empty] | 21
2016-01-18 | 1940 | [13 empty] | 0
2016-01-19 | 1467 | 0.64 | 1 | 7.1 | 3 | 4 | 2 | 6.4 | 0.11 | 2.938 | 9.4016 | 1.469 | 0.16159 | 5.876 | 0 | 2016-01-28 | 2016-01-28
2016-01-20 | 1247 | [13 empty] | 0
2016-01-21 | 1291 | [13 empty] | 0
2016-01-22 | 1117 | [13 empty] | 0
2016-01-23 | 1028 | [13 empty] | 0
2016-01-24 | 1856 | [13 empty] | 0
2016-01-25 | 1502 | [13 empty] | 7
2016-01-26 | 995 | [13 empty] | 0
2016-01-27 | 1465 | [13 empty] | 0
2016-01-28 | 1272 | [13 empty] | 0
2016-01-29 | 779 | [13 empty] | 0
2016-01-30 | 924 | [13 empty] | 4
2016-01-31 | 2035 | [13 empty] | 53
2016-02-01 | 1610 | [13 empty] | 4
2016-02-02 | 1380 | 0.3 | 1 | 7 | 1 | 6 | 2 | 4.1 | 0.15 | 2.716 | 5.5678 | 1.358 | 0.2037 | 8.148 | 0 | 2016-02-11 | 2016-02-25
2016-02-03 | 808 | [13 empty] | 0
2016-02-04 | 1323 | [13 empty] | 2
2016-02-05 | 1278 | [13 empty] | 0
2016-02-06 | 1526 | [13 empty] | 0
2016-02-07 | 1100 | [13 empty] | 9
2016-02-08 | 1852 | [13 empty] | 22
2016-02-09 | 1280 | [13 empty] | 0
2016-02-10 | 1192 | [13 empty] | 0
2016-02-11 | 1206 | [13 empty] | 0
2016-02-12 | 1214 | [13 empty] | 0
2016-02-13 | 1082 | [13 empty] | 0
2016-02-14 | 1446 | [13 empty] | 11
2016-02-15 | 1148 | [13 empty] | 0
2016-02-16 | 1302 | 0.38 | 1 | 7 | 200 | 7 | 2 | 4.5 | 0.13 | 2.482 | 5.5845 | 1.241 | 0.16133 | 8.687 | 0 | 2016-02-26 | 2016-03-11
2016-02-17 | 1165 | [13 empty] | 0
2016-02-18 | 1432 | [13 empty] | 0
2016-02-19 | 1122 | [13 empty] | 0
2016-02-20 | 1314 | [13 empty] | 1
2016-02-21 | 1519 | [13 empty] | 0
2016-02-22 | 682 | [13 empty] | 0
2016-02-23 | 1678 | [13 empty] | 1
2016-02-24 | 1307 | [13 empty] | 0
2016-02-25 | 1090 | [13 empty] | 0
2016-02-26 | 911 | [13 empty] | 0
2016-02-27 | 1129 | [13 empty] | 0
2016-02-28 | 1579 | [13 empty] | 18
2016-02-29 | 1211 | [13 empty] | 6
2016-03-01 | 1184 | 0.51 | 1 | 7.1 | 7 | 9 | 2 | 5.8 | 0.25 | 2.364 | 6.8556 | 1.182 | 0.2955 | 10.638 | 31 | 2016-03-07 | 2016-03-11
2016-03-02 | 1392 | [13 empty] | 9
2016-03-03 | 1054 | [13 empty] | 41
2016-03-04 | 1937 | [13 empty] | 5
2016-03-05 | 1117 | [13 empty] | 0
2016-03-06 | 1454 | [13 empty] | 0
2016-03-07 | 1177 | [13 empty] | 7
2016-03-08 | 1250 | [13 empty] | 12
2016-03-09 | 1450 | [13 empty] | 26
2016-03-10 | 1191 | [13 empty] | 0
2016-03-11 | 1491 | [13 empty] | 1
2016-03-12 | 1420 | [13 empty] | 0
2016-03-13 | 1163 | [13 empty] | 0
2016-03-14 | 1369 | [13 empty] | 0
2016-03-15 | 1307 | 0.6 | 1 | 7 | 2 | 5 | 2 | 4.2 | 0.14 | 2.638 | 5.5398 | 1.319 | 0.18466 | 6.595 | 11 | 2016-03-22 | 2016-04-06
2016-03-16 | 1256 | [13 empty] | 0
2016-03-17 | 2086 | [13 empty] | 47
2016-03-18 | 2143 | [13 empty] | 39
2016-03-19 | 1745 | [13 empty] | 9
2016-03-20 | 1576 | [13 empty] | 10
2016-03-21 | 1614 | [13 empty] | 0
2016-03-22 | 1765 | [13 empty] | 12
2016-03-23 | 1354 | [13 empty] | 5
2016-03-24 | 1843 | [13 empty] | 6
2016-03-25 | 1291 | [13 empty] | 0
2016-03-26 | 1847 | [13 empty] | 0
2016-03-27 | 2155 | [13 empty] | 0
2016-03-28 | 1549 | [13 empty] | 4
2016-03-29 | 1685 | 0.9 | 1 | 7.2 | 1 | 5 | 2 | 6.6 | 0.18 | 3.338 | 11.0154 | 1.669 | 0.30042 | 8.345 | 0 | 2016-04-19 | 2016-05-03
2016-03-30 | 1266 | [13 empty] | 0
2016-03-31 | 1779 | [13 empty] | 0
2016-04-01 | 1612 | [13 empty] | 22
2016-04-02 | 1302 | [13 empty] | 0
2016-04-03 | 1488 | [13 empty] | 0
2016-04-04 | 1816 | [13 empty] | 0
2016-04-05 | 1321 | [13 empty] | 0
2016-04-06 | 1253 | [13 empty] | 0
2016-04-07 | 1675 | [13 empty] | 0
2016-04-08 | 1415 | [13 empty] | 0
2016-04-09 | 1363 | [13 empty] | 0
2016-04-10 | 1483 | [13 empty] | 0
2016-04-11 | 1250 | [13 empty] | 0
2016-04-12 | 1237 | 0.18 | 1 | 7 | 1 | 5 | 2 | 4.6 | 0.16 | 2.532 | 5.8236 | 1.266 | 0.20256 | 6.33 | 1 | 2016-04-28 | 2016-05-03
2016-04-13 | 1611 | [13 empty] | 7
2016-04-14 | 2639 | [13 empty] | 87
2016-04-15 | 1899 | [13 empty] | 8
2016-04-16 | 2139 | [13 empty] | 3
2016-04-17 | 1678 | [13 empty] | 3
2016-04-18 | 1827 | [13 empty] | 0
2016-04-19 | 1850 | [13 empty] | 0
2016-04-20 | 1434 | [13 empty] | 6
2016-04-21 | 1410 | [13 empty] | 0
2016-04-22 | 1582 | [13 empty] | 2
2016-04-23 | 1618 | [13 empty] | 1
2016-04-24 | 1645 | [13 empty] | 0
2016-04-25 | 1813 | [13 empty] | 0
2016-04-26 | 1566 | 0.33 | 1 | 7.4 | 1 | 2 | 3 | 6.1 | 0.13 | 4.56 | 9.272 | 1.52 | 0.1976 | 3.04 | 6 | 2016-05-10 | 2016-05-24
2016-04-27 | 1612 | [13 empty] | 0
2016-04-28 | 1083 | [13 empty] | 0
2016-04-29 | 1770 | [13 empty] | 16
2016-04-30 | 1289 | [13 empty] | 0
2016-05-01 | 1715 | [13 empty] | 0
2016-05-02 | 1306 | [13 empty] | 0
2016-05-03 | 1492 | [13 empty] | 0
2016-05-04 | 1623 | [13 empty] | 6
2016-05-05 | 1472 | [13 empty] | 0
2016-05-06 | 1117 | [13 empty] | 0
2016-05-07 | 1400 | [13 empty] | 0
2016-05-08 | 1396 | [13 empty] | 0
2016-05-09 | 1372 | [13 empty] | 0
2016-05-10 | 1344 | 0.23 | 1 | 6.9 | 1 | 5 | 2 | 4.8 | 0.17 | 2.794 | 6.7056 | 1.397 | 0.23749 | 6.985 | 0 | 2016-05-17 | 2016-05-24
2016-05-11 | 1543 | [13 empty] | 0
2016-05-12 | 1468 | [13 empty] | 0
2016-05-13 | 1111 | [13 empty] | 0
2016-05-14 | 1250 | [13 empty] | 0
2016-05-15 | 1445 | [13 empty] | 0
2016-05-16 | 1243 | [13 empty] | 0
2016-05-17 | 1226 | [13 empty] | 0
2016-05-18 | 1221 | [13 empty] | 0
2016-05-19 | 1241 | [13 empty] | 0
2016-05-20 | 1055 | [13 empty] | 0
2016-05-21 | 1423 | [13 empty] | 0
2016-05-22 | 624 | [13 empty] | 0
2016-05-23 | 1892 | [13 empty] | 0
2016-05-24 | 618 | 0.27 | 1 | 7.3 | 1 | 3 | 2 | 4.6 | 0.11 | 2.592 | 5.9616 | 1.296 | 0.14256 | 3.888 | 0 | 2016-05-30 | 2016-06-10
2016-05-25 | 1651 | [13 empty] | 0
2016-05-26 | 1188 | [13 empty] | 0
2016-05-27 | 1121 | [13 empty] | 0
2016-05-28 | 1231 | [13 empty] | 7
2016-05-29 | 1053 | [13 empty] | 0
2016-05-30 | 1521 | [13 empty] | 0
2016-05-31 | 1135 | [13 empty] | 0
MINIMUM | 430 | 0.18 | 1 | 6.7 | 1 | 1 | 2 | 2.7 | 0.05 | 2.152 | 3.2535 | 1.062 | 0.076 | 1.076 | 0
AVERAGE | 1362.1781 | 0.55889 | 1 | 7.1444 | 21.1111 | 4.5556 | 2.2222 | 5.1926 | 0.1563 | 3.0184 | 7.1023 | 1.3594 | 0.20795 | 6.0439 | 3.2541
MAXIMUM | 2639 | 1.8 | 1 | 8.5 | 200 | 12 | 4 | 7 | 0.45 | 5.364 | 11.0154 | 1.669 | 0.60345 | 14.751 | 87
| Sample Count | 27 | [6 empty] | Total | 81.497 | 191.7626 | 36.704 | 5.6148 | 163.185 | 1191

## 16-17
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 16/17
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Date analysis results obtained | Date Published
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | -
2016-06-01 | 1164 | [13 empty] | 0
2016-06-02 | 1179 | [13 empty] | 0
2016-06-03 | 1093 | [13 empty] | 9
2016-06-04 | 888 | [13 empty] | 3
2016-06-05 | 4543 | [13 empty] | 25
2016-06-06 | 7427 | 0.35 | 2 | 6.7 | 4 | 19 | 6 | 4.9 | 0.58 | 7.398 | 6.0417 | 2.466 | 0.71514 | 23.427 | 215 | 2016-06-10 | 2016-06-24
2016-06-07 | 3199 | [13 empty] | 0
2016-06-08 | 2411 | [13 empty] | 0
2016-06-09 | 2394 | [13 empty] | 0
2016-06-10 | 2168 | [13 empty] | 0
2016-06-11 | 1960 | [13 empty] | 0
2016-06-12 | 2460 | [13 empty] | 0
2016-06-13 | 1629 | [13 empty] | 0
2016-06-14 | 1853 | [13 empty] | 7
2016-06-15 | 2124 | [13 empty] | 5
2016-06-16 | 1386 | [13 empty] | 3
2016-06-17 | 1978 | [13 empty] | 0
2016-06-18 | 1727 | [13 empty] | 0
2016-06-19 | 1426 | [13 empty] | 0
2016-06-20 | 2538 | [13 empty] | 0
2016-06-21 | 2631 | 1.1 | 2 | 7 | 1 | 6 | 4 | 5.6 | 0.14 | 7.112 | 9.9568 | 3.556 | 0.24892 | 10.668 | 32 | 2016-06-28 | 2016-07-12
2016-06-22 | 1839 | [13 empty] | 0
2016-06-23 | 1999 | [13 empty] | 0
2016-06-24 | 1389 | [13 empty] | 0
2016-06-25 | 1558 | [13 empty] | 0
2016-06-26 | 1808 | [13 empty] | 0
2016-06-27 | 1502 | [13 empty] | 0
2016-06-28 | 1843 | [13 empty] | 0
2016-06-29 | 1414 | [13 empty] | 2
2016-06-30 | 1490 | [13 empty] | 0
2016-07-01 | 1505 | [13 empty] | 0
2016-07-02 | 1526 | [13 empty] | 0
2016-07-03 | 1634 | [13 empty] | 0
2016-07-04 | 1660 | [13 empty] | 0
2016-07-05 | 1275 | 0.98 | 2 | 7 | 2 | 5 | 2 | 4.5 | 0.14 | 3.244 | 7.299 | 3.244 | 0.22708 | 8.11 | 0 | 2016-07-14 | 2016-07-28
2016-07-06 | 1370 | [13 empty] | 2
2016-07-07 | 1579 | [13 empty] | 0
2016-07-08 | 1812 | [13 empty] | 0
2016-07-09 | 1132 | [13 empty] | 0
2016-07-10 | 1675 | [13 empty] | 6
2016-07-11 | 1601 | [13 empty] | 0
2016-07-12 | 1388 | [13 empty] | 0
2016-07-13 | 1145 | [13 empty] | 0
2016-07-14 | 1663 | [13 empty] | 0
2016-07-15 | 1178 | [13 empty] | 0
2016-07-16 | 1723 | [13 empty] | 0
2016-07-17 | 1327 | [13 empty] | 0
2016-07-18 | 1368 | [13 empty] | 3
2016-07-19 | 1233 | 0.32 | 2 | 6.9 | 1 | 4 | 2 | 4.7 | 0.13 | 3.032 | 7.1252 | 3.032 | 0.19708 | 6.064 | 8 | 2016-07-26 | 2016-07-28
2016-07-20 | 1193 | [13 empty] | 0
2016-07-21 | 1365 | [13 empty] | 0
2016-07-22 | 665 | [13 empty] | 0
2016-07-23 | 2054 | [13 empty] | 0
2016-07-24 | 1068 | [13 empty] | 0
2016-07-25 | 1684 | [13 empty] | 0
2016-07-26 | 1358 | [13 empty] | 0
2016-07-27 | 1263 | [13 empty] | 0
2016-07-28 | 768 | [13 empty] | 0
2016-07-29 | 1824 | [13 empty] | 0
2016-07-30 | 1163 | [13 empty] | 0
2016-07-31 | 1479 | [13 empty] | 0
2016-08-01 | 994 | [13 empty] | 0
2016-08-02 | 1500 | 0.69 | 2 | 7 | <1 | 4 | 2 | 4.4 | 0.14 | 2.862 | 6.2964 | 2.862 | 0.20034 | 5.724 | 0 | 2016-08-10 | 2016-08-24
2016-08-03 | 1235 | [13 empty] | 0
2016-08-04 | 1235 | [13 empty] | 4
2016-08-05 | 2514 | [13 empty] | 50
2016-08-06 | 2309 | [13 empty] | 25
2016-08-07 | 1932 | [13 empty] | 16
2016-08-08 | 1577 | [13 empty] | 3
2016-08-09 | 1814 | [13 empty] | 1
2016-08-10 | 1679 | [13 empty] | 0
2016-08-11 | 1601 | [13 empty] | 0
2016-08-12 | 1557 | [13 empty] | 0
2016-08-13 | 1519 | [13 empty] | 1
2016-08-14 | 1747 | [13 empty] | 0
2016-08-15 | 1338 | [13 empty] | 0
2016-08-16 | 1663 | 0.74 | 2 | 7 | 2 | 4 | 2 | 5.5 | 0.11 | 3.104 | 8.536 | 3.104 | 0.17072 | 6.208 | 1 | 2016-08-26 | 2016-09-09
2016-08-17 | 1102 | [13 empty] | 0
2016-08-18 | 1393 | [13 empty] | 0
2016-08-19 | 1222 | [13 empty] | 0
2016-08-20 | 1904 | [13 empty] | 0
2016-08-21 | 1216 | [13 empty] | 0
2016-08-22 | 1216 | [13 empty] | 0
2016-08-23 | 1710 | [13 empty] | 0
2016-08-24 | 1372 | [13 empty] | 7
2016-08-25 | 2401 | [13 empty] | 35
2016-08-26 | 2252 | [13 empty] | 25
2016-08-27 | 1425 | [13 empty] | 0
2016-08-28 | 1699 | [13 empty] | 0
2016-08-29 | 1849 | [13 empty] | 0
2016-08-30 | 1361 | 0.63 | 2 | 7 | 1 | 6 | 2 | 4.6 | 0.11 | 3.712 | 8.5376 | 3.712 | 0.20416 | 11.136 | 0 | 2016-09-14 | 2016-09-28
2016-08-31 | 1459 | [13 empty] | 0
2016-09-01 | 1784 | [13 empty] | 0
2016-09-02 | 1042 | [13 empty] | 0
2016-09-03 | 1631 | [13 empty] | 0
2016-09-04 | 1591 | [13 empty] | 4
2016-09-05 | 1149 | [13 empty] | 0
2016-09-06 | 1522 | [13 empty] | 0
2016-09-07 | 1305 | [13 empty] | 0
2016-09-08 | 1525 | [13 empty] | 1
2016-09-09 | 1290 | [13 empty] | 0
2016-09-10 | 889 | [13 empty] | 2
2016-09-11 | 1605 | [13 empty] | 0
2016-09-12 | 1512 | [13 empty] | 0
2016-09-13 | 1290 | 0.47 | 2 | 7.2 | 1 | 7 | 2 | 4.3 | 0.05 | 2.57 | 5.5255 | 2.57 | 0.06425 | 8.995 | 0 | 2016-09-27 | 2016-09-28
2016-09-14 | 1228 | [13 empty] | 0
2016-09-15 | 974 | [13 empty] | 0
2016-09-16 | 1405 | [13 empty] | 2
2016-09-17 | 1471 | [13 empty] | 5
2016-09-18 | 1037 | [13 empty] | 0
2016-09-19 | 1299 | [13 empty] | 0
2016-09-20 | 1386 | [13 empty] | 8
2016-09-21 | 1364 | [13 empty] | 0
2016-09-22 | 1277 | [13 empty] | 3
2016-09-23 | 1595 | [13 empty] | 0
2016-09-24 | 1363 | [13 empty] | 0
2016-09-25 | 1359 | [13 empty] | 0
2016-09-26 | 1165 | [13 empty] | 1
2016-09-27 | 1563 | 0.57 | 2 | 7.2 | 1 | 4 | 2 | 9.2 | 0.12 | 2.832 | 13.0272 | 2.832 | 0.16992 | 5.664 | 0 | 2016-10-07 | 2016-10-21
2016-09-28 | 1140 | [13 empty] | 0
2016-09-29 | 1365 | [13 empty] | 0
2016-09-30 | 1528 | [13 empty] | 0
2016-10-01 | 1192 | [13 empty] | 0
2016-10-02 | 1633 | [13 empty] | 0
2016-10-03 | 1633 | [13 empty] | 6
2016-10-04 | 1560 | [13 empty] | 0
2016-10-05 | 1367 | [13 empty] | 0
2016-10-06 | 1439 | [13 empty] | 0
2016-10-07 | 920 | [13 empty] | 0
2016-10-08 | 1482 | [13 empty] | 0
2016-10-09 | 1210 | [13 empty] | 0
2016-10-10 | 1152 | [13 empty] | 2
2016-10-11 | 1239 | 0.78 | 2 | 7.4 | 5 | 6 | 2 | 5 | 0.1 | 2.49 | 6.225 | 2.49 | 0.1245 | 7.47 | 0 | 2016-10-21 | 2016-10-21
2016-10-12 | 1078 | [13 empty] | 0
2016-10-13 | 1259 | [13 empty] | 0
2016-10-14 | 877 | [13 empty] | 0
2016-10-15 | 1589 | [13 empty] | 0
2016-10-16 | 1092 | [13 empty] | 0
2016-10-17 | 1308 | [13 empty] | 0
2016-10-18 | 1226 | [13 empty] | 0
2016-10-19 | 1361 | [13 empty] | 3
2016-10-20 | 1130 | [13 empty] | 0
2016-10-21 | 751 | [13 empty] | 0
2016-10-22 | 1683 | [13 empty] | 0
2016-10-23 | 1099 | [13 empty] | 0
2016-10-24 | 1110 | [13 empty] | 4
2016-10-25 | 1351 | 0.72 | 2 | 7.2 | 24 | 6 | 2 | 6.4 | 0.08 | 2.372 | 7.5904 | 2.372 | 0.09488 | 7.116 | 0 | 2016-11-04 | 2016-11-18
2016-10-26 | 713 | [13 empty] | 0
2016-10-27 | 1350 | [13 empty] | 0
2016-10-28 | 1306 | [13 empty] | 2
2016-10-29 | 1112 | [13 empty] | 9
2016-10-30 | 1191 | [13 empty] | 0
2016-10-31 | 642 | [13 empty] | 0
2016-11-01 | 1556 | [13 empty] | 0
2016-11-02 | 1163 | [13 empty] | 0
2016-11-03 | 1122 | [13 empty] | 0
2016-11-04 | 1284 | [13 empty] | 0
2016-11-05 | 871 | [13 empty] | 0
2016-11-06 | 1512 | [13 empty] | 0
2016-11-07 | 1205 | [13 empty] | 0
2016-11-08 | 1015 | 0.47 | 2 | 8.2 | 1 | 5 | 2 | 5.3 | 0.12 | 2.244 | 5.9466 | 2.244 | 0.13464 | 5.61 | 0 | 2016-11-24 | 2016-12-08
2016-11-09 | 1354 | [13 empty] | 0
2016-11-10 | 1095 | [13 empty] | 27
2016-11-11 | 835 | [13 empty] | 0
2016-11-12 | 1464 | [13 empty] | 0
2016-11-13 | 1578 | [13 empty] | 5
2016-11-14 | 1072 | [13 empty] | 0
2016-11-15 | 1190 | [13 empty] | 1
2016-11-16 | 1249 | [13 empty] | 3
2016-11-17 | 1037 | [13 empty] | 2
2016-11-18 | 861 | [13 empty] | 0
2016-11-19 | 1312 | [13 empty] | 0
2016-11-20 | 1174 | [13 empty] | 0
2016-11-21 | 1201 | [13 empty] | 0
2016-11-22 | 1227 | 0.77 | ,2 | 6.9 | ,1 | 5 | 2 | 10 | 0.13 | 2.35 | 11.75 | 2.35 | 0.15275 | 5.875 | 0 | 2016-11-30 | 2016-12-08
2016-11-23 | 634 | [13 empty] | 0
2016-11-24 | 483 | [13 empty] | 0
2016-11-25 | 1351 | [13 empty] | 0
2016-11-26 | 659 | [13 empty] | 0
2016-11-27 | 1499 | [13 empty] | 0
2016-11-28 | 1114 | [13 empty] | 0
2016-11-29 | 1163 | [13 empty] | 8
2016-11-30 | 1211 | [13 empty] | 0
2016-12-01 | 1033 | [13 empty] | 0
2016-12-02 | 1176 | [13 empty] | 1
2016-12-03 | 1121 | [13 empty] | 0
2016-12-04 | 1324 | [13 empty] | 4
2016-12-05 | 1157 | [13 empty] | 0
2016-12-06 | 1177 | 0.49 | 2 | 7.7 | 1 | 9 | 4 | 6.3 | 0.17 | 5.336 | 8.4042 | 2.668 | 0.22678 | 12.006 | 0 | 2016-12-15 | 2016-12-29
2016-12-07 | 1363 | [13 empty] | 21
2016-12-08 | 1164 | [13 empty] | 0
2016-12-09 | 1743 | [13 empty] | 15
2016-12-10 | 1598 | [13 empty] | 7
2016-12-11 | 1336 | [13 empty] | 0
2016-12-12 | 1189 | [13 empty] | 0
2016-12-13 | 1225 | [13 empty] | 0
2016-12-14 | 1243 | [13 empty] | 0
2016-12-15 | 1261 | [13 empty] | 0
2016-12-16 | 1139 | 0.45 | 2 | 7 | 3 | 5 | 2 | 5.8 | 0.21 | 2.442 | 7.0818 | 2.442 | 0.25641 | 6.105 | 0 | 2016-12-23 | 2016-12-29
2016-12-17 | 1287 | [13 empty] | 0
2016-12-18 | 616 | [13 empty] | 0
2016-12-19 | 1778 | [13 empty] | 0
2016-12-20 | 1199 | [13 empty] | 0
2016-12-21 | 1141 | [13 empty] | 0
2016-12-22 | 990 | [13 empty] | 0
2016-12-23 | 1254 | [13 empty] | 0
2016-12-24 | 1316 | [13 empty] | 0
2016-12-25 | 745 | [13 empty] | 0
2016-12-26 | 1325 | [13 empty] | 0
2016-12-27 | 1447 | [13 empty] | 0
2016-12-28 | 1405 | [13 empty] | 0
2016-12-29 | 1346 | [13 empty] | 0
2016-12-30 | 1502 | [13 empty] | 0
2016-12-31 | 943 | [13 empty] | 0
2017-01-01 | 1722 | [13 empty] | 0
2017-01-02 | 1099 | 5.4 |  |  |  |  | 2 | 11 | 0.12 | 2.99 | 16.445 |  | 0.1794 |  | 0 | 2017-01-16 | 2017-01-30
2017-01-03 | 352 | 1.5 | 2 | 7 | 1 | 3 | 2 | 9.3 | 0.14 | 2.986 | 13.8849 | 2.986 | 0.20902 | 4.479 | 0 | 2017-01-16 | 2017-01-30
2017-01-04 | 642 | [13 empty] | 23
2017-01-05 | 1807 | [13 empty] | 0
2017-01-06 | 1506 | [13 empty] | 0
2017-01-07 | 1517 | [13 empty] | 26
2017-01-08 | 1363 | [13 empty] | 9
2017-01-09 | 1979 | [13 empty] | 9
2017-01-10 | 1609 | [13 empty] | 0
2017-01-11 | 1450 | [13 empty] | 0
2017-01-12 | 1595 | [13 empty] | 3
2017-01-13 | 1439 | [13 empty] | 8
2017-01-14 | 1718 | [13 empty] | 0
2017-01-15 | 1355 | [13 empty] | 0
2017-01-16 | 1505 | 0.77 | 1 | 7.2 | 1 | 4 | 1 | 8.9 | 0.12 | 1.64 | 14.59 | 1.64 | 0.2 | 6.56 | 0 | 2017-02-01 | 2017-02-15
2017-01-17 | 1116 | [13 empty] | 0
2017-01-18 | 1754 | [13 empty] | 0
2017-01-19 | 1351 | [13 empty] | 0
2017-01-20 | 981 | [13 empty] | 0
2017-01-21 | 1257 | [13 empty] | 0
2017-01-22 | 960 | [13 empty] | 12
2017-01-23 | 1233 | [13 empty] | 0
2017-01-24 | 1301 | [13 empty] | 0
2017-01-25 | 1565 | [13 empty] | 0
2017-01-26 | 1044 | [13 empty] | 0
2017-01-27 | 1427 | [13 empty] | 16
2017-01-28 | 1493 | [13 empty] | 0
2017-01-29 | 1210 | [13 empty] | 0
2017-01-30 | 1160 | 0.29 | 1 | 7.1 | 1 | 4 | 1 | 4.4 | 0.13 | 1.4 | 6.16 | 1.4 | 0.18 | 5.6 | 0 | 2017-02-14 | 2017-02-15
2017-01-31 | 1399 | [13 empty] | 0
2017-02-01 | 1015 | [13 empty] | 0
2017-02-02 | 1234 | [13 empty] | 0
2017-02-03 | 1176 | [13 empty] | 0
2017-02-04 | 910 | [13 empty] | 0
2017-02-05 | 1082 | [13 empty] | 0
2017-02-06 | 1456 | [13 empty] | 0
2017-02-07 | 1066 | [13 empty] | 0
2017-02-08 | 1061 | [13 empty] | 0
2017-02-09 | 683 | [13 empty] | 0
2017-02-10 | 1084 | [13 empty] | 4
2017-02-11 | 1222 | [13 empty] | 0
2017-02-12 | 1086 | [13 empty] | 0
2017-02-13 | 1095 | 0.36 | 1 | 7.4 | 30 | 2 | 1 | 4.3 | 0.15 | 1.12 | 4.816 | 1.12 | 0.168 | 2.24 | 0 | 2017-02-27 | 2017-03-14
2017-02-14 | 1320 | [13 empty] | 0
2017-02-15 | 874 | [13 empty] | 2
2017-02-16 | 1056 | [13 empty] | 0
2017-02-17 | 864 | [13 empty] | 0
2017-02-18 | 1188 | [13 empty] | 0
2017-02-19 | 1417 | [13 empty] | 2
2017-02-20 | 1036 | [13 empty] | 0
2017-02-21 | 1094 | [13 empty] | 3
2017-02-22 | 1142 | [13 empty] | 3
2017-02-23 | 1165 | [13 empty] | 7
2017-02-24 | 619 | [13 empty] | 0
2017-02-25 | 1381 | [13 empty] | 0
2017-02-26 | 1130 | [13 empty] | 0
2017-02-27 | 1079 | 0.6 | 1 | 7.3 | 1 | 4 | 2 | 5.3 | 0.18 | 2.33 | 6.16 | 1.16 | 0.21 | 4.65 | 0 | 2017-03-08 | 2017-03-17
2017-02-28 | 1923 | [13 empty] | 38
2017-03-01 | 2336 | [13 empty] | 92
2017-03-02 | 1799 | [13 empty] | 38
2017-03-03 | 2136 | [13 empty] | 1
2017-03-04 | 1481 | [13 empty] | 2
2017-03-05 | 1568 | [13 empty] | 0
2017-03-06 | 1253 | [13 empty] | 1
2017-03-07 | 1370 | [13 empty] | 6
2017-03-08 | 1484 | [13 empty] | 0
2017-03-09 | 1331 | [13 empty] | 0
2017-03-10 | 1112 | [13 empty] | 2
2017-03-11 | 1489 | [13 empty] | 5
2017-03-12 | 1164 | [13 empty] | 0
2017-03-13 | 1314 | [13 empty] | 0
2017-03-14 | 1114 | 0.19 | 1 | 7.1 | <1 | 4 | 1 | 4.6 | 0.13 | 1.378 | 6.3388 | 1.378 | 0.17914 | 5.512 | 0 | 2017-03-28 | 2017-03-28
2017-03-15 | 1566 | [13 empty] | 10
2017-03-16 | 3746 | [13 empty] | 58
2017-03-17 | 2871 | [13 empty] | 100
2017-03-18 | 2130 | [13 empty] | 0
2017-03-19 | 6758 | [13 empty] | 48
2017-03-20 | 5404 | [13 empty] | 163
2017-03-21 | 4285 | [13 empty] | 26
2017-03-22 | 3722 | [13 empty] | 2
2017-03-23 | 3221 | [13 empty] | 0
2017-03-24 | 2778 | [13 empty] | 1
2017-03-25 | 2322 | [13 empty] | 1
2017-03-26 | 2562 | [13 empty] | 11
2017-03-27 | 2118 | 0.25 | 1 | 7.1 | 1 | 4 | 2 | 4.6 | 0.18 | 5.404 | 12.4292 | 2.702 | 0.48636 | 10.808 | 0 | 2017-04-04 | 2017-04-04
2017-03-28 | 1846 | [13 empty] | 0
2017-03-29 | 2450 | [13 empty] | 0
2017-03-30 | 1247 | [13 empty] | 15
2017-03-31 | 6146 | [13 empty] | 252
2017-04-01 | 8453 | [13 empty] | 0
2017-04-02 | 6712 | [13 empty] | 0
2017-04-03 | 5735 | [13 empty] | 0
2017-04-04 | 6603 | [13 empty] | 0
2017-04-05 | 5880 | [13 empty] | 17
2017-04-06 | 6682 | [13 empty] | 31
2017-04-07 | 6218 | [13 empty] | 28
2017-04-08 | 4666 | [13 empty] | 6
2017-04-09 | 3552 | [13 empty] | 0
2017-04-10 | 2983 | [13 empty] | 0
2017-04-11 | 2695 | 0.25 | 1 | 6.9 | 3 | 12 | 3 | 5.4 | 0.27 | 15.08 | 27.15 | 5.03 | 1.36 | 60.32 | 0 | 2017-04-24 | 2017-05-09
2017-04-12 | 2712 | [13 empty] | 0
2017-04-13 | 2881 | [13 empty] | 0
2017-04-14 | 3101 | [13 empty] | 9
2017-04-15 | 2392 | [13 empty] | 0
2017-04-16 | 2346 | [13 empty] | 0
2017-04-17 | 2029 | [13 empty] | 0
2017-04-18 | 2257 | [13 empty] | 1
2017-04-19 | 1955 | [13 empty] | 0
2017-04-20 | 1735 | [13 empty] | 0
2017-04-21 | 1526 | [13 empty] | 2
2017-04-22 | 1801 | [13 empty] | 0
2017-04-23 | 1822 | [13 empty] | 0
2017-04-24 | 1998 | [13 empty] | 0
2017-04-25 | 1546 | 0.35 | 1 | 7 | 1 | 6 | 2 | 5.7 | 0.19 | 3.73 | 10.62 | 1.864 | 0.35 | 11.18 | 0 | 2017-04-24 | 2017-05-09
2017-04-26 | 1690 | [13 empty] | 0
2017-04-27 | 1353 | [13 empty] | 0
2017-04-28 | 2240 | [13 empty] | 7
2017-04-29 | 1528 | [13 empty] | 0
2017-04-30 | 1848 | [13 empty] | 0
2017-05-01 | 1595 | [13 empty] | 0
2017-05-02 | 1701 | [13 empty] | 0
2017-05-03 | 1166 | [13 empty] | 0
2017-05-04 | 1659 | [13 empty] | 0
2017-05-05 | 1504 | [13 empty] | 19
2017-05-06 | 1401 | [13 empty] | 5
2017-05-07 | 1780 | [13 empty] | 7
2017-05-08 | 1442 | [13 empty] | 0
2017-05-09 | 1496 | 0.31 | 1 | 6.7 | 1 | 6 | 2 | 4.6 | 0.09 | 3.33 | 7.65 | 1.663 | 0.15 | 9.98 | 0 | 2017-05-16 | 2017-05-22
2017-05-10 | 1661 | [13 empty] | 0
2017-05-11 | 1777 | [13 empty] | 10
2017-05-12 | 1554 | [13 empty] | 10
2017-05-13 | 1309 | [13 empty] | 3
2017-05-14 | 1728 | [13 empty] | 3
2017-05-15 | 1781 | [13 empty] | 19
2017-05-16 | 1480 | [13 empty] | 8
2017-05-17 | 1686 | [13 empty] | 5
2017-05-18 | 1751 | [13 empty] | 0
2017-05-19 | 1577 | [13 empty] | 0
2017-05-20 | 1250 | [13 empty] | 1
2017-05-21 | 2082 | [13 empty] | 14
2017-05-22 | 1350 | [13 empty] | 0
2017-05-23 | 1703 | 0.36 | 1 | 6.9 | 1 | 5 | 2 | 4.1 | 0.12 | 3.15 | 6.46 | 1.58 | 0.19 | 7.88 | 0 | 2017-05-23 | 2017-05-29
2017-05-24 | 1296 | [13 empty] | 2
2017-05-25 | 1704 | [13 empty] | 0
2017-05-26 | 1353 | [13 empty] | 0
2017-05-27 | 1424
2017-05-28 | 1650
2017-05-29 | 1494
2017-05-30 | 1227
2017-05-31 | 1408
MINIMUM | 352 | 0.19 | 1 | 6.7 | 1 | 2 | 1 | 4.1 | 0.05 | 1.12 | 4.816 | 1.12 | 0.06425 | 2.24 | 0
AVERAGE | 1656.5863 | 0.74667 | 1.6 | 7.1192 | 3.8261 | 5.7308 | 2.1852 | 5.8778 | 0.1537 | 3.6162 | 9.3351 | 2.4795 | 0.26109 | 9.9764 | 5.1111
MAXIMUM | 8453 | 5.4 | 2 | 8.2 | 30 | 19 | 6 | 11 | 0.58 | 15.08 | 27.15 | 5.03 | 1.36 | 60.32 | 252
| Sample Count | 27 | [6 empty] | Total | 97.638 | 252.0473 | 64.467 | 7.0495 | 259.387 | 1840

## 17-18
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 17/18
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | - | -
2017-06-01 | 1553 | [13 empty] | 0
2017-06-02 | 1175 | [13 empty] | 0
2017-06-03 | 1345 | [13 empty] | 0
2017-06-04 | 1533 | [13 empty] | 0
2017-06-05 | 828 | 0.41 | 1 | 7 | 1 | 2 | 2 | 6.8 | 0.11 | 2.92 | 9.91 | 1.46 | 0.16 | 2.92 | 1 |  | 2017-06-20 | 2017-06-20
2017-06-06 | 1352 | [13 empty] | 1
2017-06-07 | 1562 | [13 empty] | 0
2017-06-08 | 1470 | [13 empty] | 0
2017-06-09 | 1514 | [13 empty] | 0
2017-06-10 | 1423 | [13 empty] | 0
2017-06-11 | 4300 | [13 empty] | 98
2017-06-12 | 6110 | [13 empty] | 58
2017-06-13 | 7700 | [13 empty] | 76
2017-06-14 | 7494 | [13 empty] | 112
2017-06-15 | 3884 | [13 empty] | 1
2017-06-16 | 3373 | [13 empty] | 0
2017-06-17 | 3444 | [13 empty] | 2
2017-06-18 | 3364 | [13 empty] | 14
2017-06-19 | 3570 | 0.12 | 1 | 7 | 1 | 5 | 2 | 2.5 | 0.14 | 7.2 | 9 | 3.6 | 0.5 | 17.99 | 21 |  | 2017-06-28 | 2017-06-28
2017-06-20 | 3161 | [13 empty] | 7
2017-06-21 | 4220 | [13 empty] | 23
2017-06-22 | 3701 | [13 empty] | 10
2017-06-23 | 2910 | [13 empty] | 0
2017-06-24 | 2203 | [13 empty] | 0
2017-06-25 | 2403 | [13 empty] | 0
2017-06-26 | 2278 | [13 empty] | 0
2017-06-27 | 2190 | [13 empty] | 0
2017-06-28 | 2989 | [13 empty] | 1
2017-06-29 | 2690 | [13 empty] | 0
2017-06-30 | 1976 | [13 empty] | 0
2017-07-01 | 2603 | [13 empty] | 11
2017-07-02 | 1831 | [13 empty] | 0
2017-07-03 | 1917 | 0.37 | 1 | 6.9 | 1 | 4 | 2 | 5 | 0.1 | 2.19 | 11.94 | 2.19 | 0.24 | 9.55 | 0 |  | 2017-07-13 | 2017-07-13
2017-07-04 | 1847 | [13 empty] | 0
2017-07-05 | 2003 | [13 empty] | 1
2017-07-06 | 1784 | [13 empty] | 0
2017-07-07 | 2029 | [13 empty] | 0
2017-07-08 | 1725 | [13 empty] | 0
2017-07-09 | 1775 | [13 empty] | 0
2017-07-10 | 1558 | [13 empty] | 0
2017-07-11 | 1626 | [13 empty] | 0
2017-07-12 | 1623 | [13 empty] | 0
2017-07-13 | 1809 | [13 empty] | 0
2017-07-14 | 1574 | [13 empty] | 1
2017-07-15 | 1825 | [13 empty] | 0
2017-07-16 | 1649 | [13 empty] | 0
2017-07-17 | 1280 | 0.56 | 1 | 7 | 2 | 4 | 2 | 5.3 | 0.11 | 3.92 | 10.38 | 1.71 | 0.22 | 7.83 | 0 |  | 2017-07-27 | 2017-07-27
2017-07-18 | 1738 | [13 empty] | 0
2017-07-19 | 1538 | [13 empty] | 1
2017-07-20 | 1363 | [13 empty] | 0
2017-07-21 | 1861 | [13 empty] | 0
2017-07-22 | 1169 | [13 empty] | 0
2017-07-23 | 1637 | [13 empty] | 0
2017-07-24 | 1600 | [13 empty] | 0
2017-07-25 | 1406 | [13 empty] | 0
2017-07-26 | 1133 | [13 empty] | 0
2017-07-27 | 1423 | [13 empty] | 0
2017-07-28 | 1426 | [13 empty] | 0
2017-07-29 | 1138 | [13 empty] | 0
2017-07-30 | 1634 | [13 empty] | 0
2017-07-31 | 1524 | 0.76 | 1 | 7 | 4 | 8 | 2 | 6.1 | 0.17 | 3.09 | 9.42 | 1.54 | 0.25806 | 12.35 | 0 |  | 2017-08-14 | 2017-08-14
2017-08-01 | 1237 | [13 empty] | 0
2017-08-02 | 1628 | [13 empty] | 1
2017-08-03 | 1196 | [13 empty] | 0
2017-08-04 | 1168 | [13 empty] | 0
2017-08-05 | 1770 | [13 empty] | 0
2017-08-06 | 1360 | [13 empty] | 0
2017-08-07 | 1154 | [13 empty] | 0
2017-08-08 | 1619 | [13 empty] | 0
2017-08-09 | 1219 | [13 empty] | 0
2017-08-10 | 1419 | [13 empty] | 0
2017-08-11 | 1283 | [13 empty] | 0
2017-08-12 | 1422 | [13 empty] | 0
2017-08-13 | 1299 | [13 empty] | 0
2017-08-14 | 1511 | 1.2 | 1 | 7.1 | 3 | 9 | 3 | 5.2 | 0.07 | 4.82 | 8.36 | 1.61 | 0.11 | 14.46 | 0 |  | 2017-08-22 | 2017-08-22
2017-08-15 | 1126 | [13 empty] | 0
2017-08-16 | 1457 | [13 empty] | 1
2017-08-17 | 1390 | [13 empty] | 0
2017-08-18 | 1062 | [13 empty] | 0
2017-08-19 | 1509 | [13 empty] | 0
2017-08-20 | 978 | [13 empty] | 0
2017-08-21 | 1244 | [13 empty] | 0
2017-08-22 | 1591 | [13 empty] | 0
2017-08-23 | 1137 | [13 empty] | 1
2017-08-24 | 1206 | [13 empty] | 0
2017-08-25 | 644 | [13 empty] | 0
2017-08-26 | 1634 | [13 empty] | 4
2017-08-27 | 1363 | [13 empty] | 1
2017-08-28 | 1178 | 1.1 | 1 | 7 | 1 | 6 | 3 | 5.3 | 0.1 | 3.98 | 7.02 | 1.33 | 0.13 | 7.95 | 0 |  | 2017-09-05 | 2017-09-05
2017-08-29 | 1178 | [13 empty] | 0
2017-08-30 | 1227 | [13 empty] | 0
2017-08-31 | 1338 | [13 empty] | 0
2017-09-01 | 1132 | [13 empty] | 0
2017-09-02 | 1225 | [13 empty] | 0
2017-09-03 | 1071 | [13 empty] | 0
2017-09-04 | 1251 | [13 empty] | 0
2017-09-05 | 1467 | [13 empty] | 0
2017-09-06 | 1117 | [13 empty] | 0
2017-09-07 | 1200 | [13 empty] | 0
2017-09-08 | 1219 | [13 empty] | 0
2017-09-09 | 1117 | [13 empty] | 0
2017-09-10 | 1187 | [13 empty] | 0
2017-09-11 | 1163 | 0.39 | 1 | 7.1 | 4 | 6 | 2 | 5.9 | 0.13 | 2.81 | 8.28 | 1.4 | 0.18 | 8.42 | 0 |  | 2017-09-20 | 2017-09-20
2017-09-12 | 1149 | [13 empty] | 0
2017-09-13 | 1063 | [13 empty] | 0
2017-09-14 | 1007 | [13 empty] | 0
2017-09-15 | 1567 | [13 empty] | 0
2017-09-16 | 1136 | [13 empty] | 0
2017-09-17 | 1192 | [13 empty] | 0
2017-09-18 | 655 | [13 empty] | 0
2017-09-19 | 1702 | [13 empty] | 0
2017-09-20 | 1317 | [13 empty] | 0
2017-09-21 | 1031 | [13 empty] | 0
2017-09-22 | 1251 | [13 empty] | 0
2017-09-23 | 1137 | [13 empty] | 1
2017-09-24 | 1637 | [13 empty] | 0
2017-09-25 | 1436 | 0.83 | 1 | 7.1 | 7 | 5 | 2 | 6.2 | 0.13 | 2.68 | 8.32 | 1.34 | 0.17 | 6.71 | 0 |  | 2017-10-06 | 2017-10-06
2017-09-26 | 1252 | [13 empty] | 0
2017-09-27 | 1423 | [13 empty] | 1
2017-09-28 | 1268 | [13 empty] | 0
2017-09-29 | 1521 | [13 empty] | 0
2017-09-30 | 1085 | [13 empty] | 0
2017-10-01 | 1275 | [13 empty] | 0
2017-10-02 | 1250 | [13 empty] | 0
2017-10-03 | 1440 | [13 empty] | 0
2017-10-04 | 1276 | [13 empty] | 25
2017-10-05 | 1295 | [13 empty] | 10
2017-10-06 | 1246 | [13 empty] | 0
2017-10-07 | 1051 | [13 empty] | 0
2017-10-08 | 1602 | [13 empty] | 0
2017-10-09 | 1164 | 0.31 | 1 | 7.1 | 33 | 2 | 1 | 5.4 | 0.18 | 1.23 | 6.66 | 1.23 | 0.22 | 2.47 | 0 |  | 2017-10-27 | 2017-10-27
2017-10-10 | 1177 | [13 empty] | 4
2017-10-11 | 1027 | [13 empty] | 4
2017-10-12 | 1080 | [13 empty] | 0
2017-10-13 | 1211 | [13 empty] | 0
2017-10-14 | 1150 | [13 empty] | 0
2017-10-15 | 989 | [13 empty] | 10
2017-10-16 | 2373 | [13 empty] | 57
2017-10-17 | 1234 | [13 empty] | 2
2017-10-18 | 1520 | [13 empty] | 6
2017-10-19 | 2018 | [13 empty] | 3
2017-10-20 | 1398 | [13 empty] | 0
2017-10-21 | 1222 | [13 empty] | 0
2017-10-22 | 1978 | [13 empty] | 29
2017-10-23 | 1760 | 0.75 | 1 | 7 | 1 | 4 | 3 | 4.6 | 0.1 | 4.23 | 6.48 | 1.41 | 0.14 | 5.64 | 7 |  | 2017-11-02 | 2017-11-06
2017-10-24 | 1464 | [13 empty] | 0
2017-10-25 | 1259 | [13 empty] | 0
2017-10-26 | 1834 | [13 empty] | 0
2017-10-27 | 1398 | [13 empty] | 0
2017-10-28 | 1169 | [13 empty] | 0
2017-10-29 | 1718 | [13 empty] | 0
2017-10-30 | 1193 | [13 empty] | 0
2017-10-31 | 1498 | [13 empty] | 0
2017-11-01 | 1216 | [13 empty] | 0
2017-11-02 | 1632 | [13 empty] | 0
2017-11-03 | 1436 | [13 empty] | 0
2017-11-04 | 1030 | [13 empty] | 0
2017-11-05 | 1664 | [13 empty] | 0
2017-11-06 | 1644 | 0.96 | 1 | 7.2 | 9 | 5 | 2 | 6.6 | 0.18 | 3.01 | 9.94 | 1.51 | 0.27 | 7.53 | 0 |  | 2017-11-17 | 2017-11-22
2017-11-07 | 1842 | [13 empty] | 38
2017-11-08 | 1734 | [13 empty] | 11
2017-11-09 | 1644 | [13 empty] | 1
2017-11-10 | 1506 | [13 empty] | 4
2017-11-11 | 1493 | [13 empty] | 6
2017-11-12 | 1739 | [13 empty] | 22
2017-11-13 | 1746 | [13 empty] | 10
2017-11-14 | 1768 | [13 empty] | 0
2017-11-15 | 1216 | [13 empty] | 0
2017-11-16 | 1696 | [13 empty] | 0
2017-11-17 | 1355 | [13 empty] | 0
2017-11-18 | 1255 | [13 empty] | 0
2017-11-19 | 1096 | [13 empty] | 0
2017-11-20 | 1621 | 0.57 | 1 | 6.9 | 1 | 2 | 2 | 3.4 | 0.12 | 1.37 | 4.67 | 1.37 | 0.16 | 2.75 | 2 |  | 2017-11-29 | 2017-12-12
2017-11-21 | 1088 | [13 empty] | 3
2017-11-22 | 1235 | [13 empty] | 0
2017-11-23 | 1659 | [13 empty] | 3
2017-11-24 | 1174 | [13 empty] | 0
2017-11-25 | 1023 | [13 empty] | 4
2017-11-26 | 1043 | [13 empty] | 0
2017-11-27 | 1116 | [13 empty] | 0
2017-11-28 | 1300 | [13 empty] | 2
2017-11-29 | 1784 | [13 empty] | 0
2017-11-30 | 999 | [13 empty] | 0
2017-12-01 | 1361 | [13 empty] | 9
2017-12-02 | 1526 | [13 empty] | 25
2017-12-03 | 1071 | [13 empty] | 0
2017-12-04 | 724 | 0.55 | 1 | 6.9 | 2 | 4 | 2 | 3.9 | 0.09 | 1.88 | 7.32 | 1.88 | 0.17 | 7.5 | 4 |  | 2017-12-14 | 2017-12-14
2017-12-05 | 1249 | [13 empty] | 0
2017-12-06 | 2035 | [13 empty] | 2
2017-12-07 | 1507 | [13 empty] | 19
2017-12-08 | 1806 | [13 empty] | 0
2017-12-09 | 978 | [13 empty] | 0
2017-12-10 | 1741 | [13 empty] | 0
2017-12-11 | 1125 | [13 empty] | 3
2017-12-12 | 1586 | [13 empty] | 0
2017-12-13 | 1229 | [13 empty] | 0
2017-12-14 | 1079 | [13 empty] | 0
2017-12-15 | 1441 | [13 empty] | 0
2017-12-16 | 1273 | [13 empty] | 0
2017-12-17 | 1446 | [13 empty] | 0
2017-12-18 | 1231 | 0.52 | 1 | 6.8 | <1 | 5 | 2 | 3.9 | 0.06 | 2.45 | 4.79 | 1.23 | 0.02 | 6.14 | 0 |  | 2018-01-09 | 2018-01-09
2017-12-19 | 1243 | [13 empty] | 0
2017-12-20 | 1389 | [13 empty] | 0
2017-12-21 | 1368 | [13 empty] | 0
2017-12-22 | 1489 | [13 empty] | 0
2017-12-23 | 1421 | [13 empty] | 33
2017-12-24 | 1586 | [13 empty] | 0
2017-12-25 | 935 | [13 empty] | 0
2017-12-26 | 1845 | [13 empty] | 3
2017-12-27 | 1674 | [13 empty] | 23
2017-12-28 | 1979 | [13 empty] | 4
2017-12-29 | 1077 | [13 empty] | 1
2017-12-30 | 1688 | [13 empty] | 0
2017-12-31 | 1680 | [13 empty] | 0
2018-01-01 | 2028 | 0.79 | 1 | 6.9 | <1 | 6 | 2 | 8.4 | 0.18 | 3.65 | 15.31 | 1.82 | 0.33 | 10.94 | 3 |  | 2018-01-11 | 2018-01-11
2018-01-02 | 1714 | [13 empty] | 3
2018-01-03 | 1926 | [13 empty] | 18
2018-01-04 | 2009 | [13 empty] | 23
2018-01-05 | 1626 | [13 empty] | 0
2018-01-06 | 1831 | [13 empty] | 0
2018-01-07 | 1603 | [13 empty] | 0
2018-01-08 | 1739 | [13 empty] | 0
2018-01-09 | 1929 | [13 empty] | 0
2018-01-10 | 1408 | [13 empty] | 0
2018-01-11 | 1691 | [13 empty] | 0
2018-01-12 | 1528 | [13 empty] | 0
2018-01-13 | 1234 | [13 empty] | 0
2018-01-14 | 1466 | [13 empty] | 0
2018-01-15 | 1721 | 0.94 | 1 | 7.2 | 1 | 6 | 2 | 7.9 | 0.2 | 3.24 | 12.78 | 1.62 | 0.32 | 9.71 | 0 |  | 2018-01-23 | 2018-01-23
2018-01-16 | 1302 | [13 empty] | 0
2018-01-17 | 1266 | [13 empty] | 0
2018-01-18 | 1415 | [13 empty] | 0
2018-01-19 | 1047 | [13 empty] | 0
2018-01-20 | 1462 | [13 empty] | 0
2018-01-21 | 1250 | [13 empty] | 2
2018-01-22 | 1354 | [13 empty] | 2
2018-01-23 | 1282 | [13 empty] | 0
2018-01-24 | 1636 | [13 empty] | 0
2018-01-25 | 1161 | [13 empty] | 0
2018-01-26 | 1473 | [13 empty] | 0
2018-01-27 | 1171 | [13 empty] | 0
2018-01-28 | 1401 | [13 empty] | 0
2018-01-29 | 1293 | 0.31 | 1 | 7.3 | <1 | 6 | 2 | 4.5 | 0.18 | 1.23 | 5.54 | 1.23 | 0.22 | 7.38 | 1 | 12.25 | 2018-02-13 | 2018-02-13
2018-01-30 | 1159 | [13 empty] | 4
2018-01-31 | 1019 | [13 empty] | 12
2018-02-01 | 1187 | [13 empty] | 0
2018-02-02 | 1317 | [13 empty] | 21
2018-02-03 | 1170 | [13 empty] | 8
2018-02-04 | 1314 | [13 empty] | 31
2018-02-05 | 1490 | [13 empty] | 15
2018-02-06 | 801 | [13 empty] | 1
2018-02-07 | 1919 | [13 empty] | 3
2018-02-08 | 1191 | [13 empty] | 0
2018-02-09 | 1345 | [13 empty] | 3
2018-02-10 | 889 | [13 empty] | 0
2018-02-11 | 1581 | [13 empty] | 0
2018-02-12 | 1205 | 0.4 | 1 | 7 | <1 | 5 | 2 | 3.8 | 0.12 | 2.53 | 4.8 | 1.26 | 0.15 | 6.32 | 1 | 11.5 | 2018-02-26 | 2018-02-26
2018-02-13 | 1155 | [13 empty] | 0
2018-02-14 | 1116 | [13 empty] | 0
2018-02-15 | 1140 | [13 empty] | 0
2018-02-16 | 1010 | [13 empty] | 0
2018-02-17 | 1163 | [13 empty] | 0
2018-02-18 | 1190 | [13 empty] | 0
2018-02-19 | 880 | [13 empty] | 0
2018-02-20 | 1555 | [13 empty] | 0
2018-02-21 | 1140 | [13 empty] | 0
2018-02-22 | 1134 | [13 empty] | 13
2018-02-23 | 789 | [13 empty] | 0
2018-02-24 | 1588 | [13 empty] | 11
2018-02-25 | 1395 | [13 empty] | 6
2018-02-26 | 1601 | <0.01 | 1 | 7.1 | <1 | 4 | 2 | 3.8 | 0.1 | 1.21 | 4.61 | 1.21 | 0.12 | 4.86 | 39 | 11.4 | 2018-03-07 | 2018-03-07
2018-02-27 | 1469 | [13 empty] | 0
2018-02-28 | 953 | [13 empty] | 21
2018-03-01 | 1727 | [13 empty] | 0
2018-03-02 | 1058 | [13 empty] | 0
2018-03-03 | 1565 | [13 empty] | 0
2018-03-04 | 1225 | [13 empty] | 7
2018-03-05 | 1151 | [13 empty] | 0
2018-03-06 | 1682 | [13 empty] | 0
2018-03-07 | 3260 | [13 empty] | 74
2018-03-08 | 3371 | [13 empty] | 41
2018-03-09 | 2298 | [13 empty] | 0
2018-03-10 | 2290 | [13 empty] | 12
2018-03-11 | 1877 | [13 empty] | 4
2018-03-12 | 2157 | 0.65 | <2 | 7.1 | 3 | 5 | <2 | 4.6 | 0.11 | 2.46 | 11.29 | 2.46 | 0.27 | 12.28 | 4 | 16.05 | 2018-03-23 | 2018-03-23
2018-03-13 | 1821 | [13 empty] | 3
2018-03-14 | 1614 | [13 empty] | 0
2018-03-15 | 1743 | [13 empty] | 3
2018-03-16 | 1619 | [13 empty] | 0
2018-03-17 | 1496 | [13 empty] | 0
2018-03-18 | 1460 | [13 empty] | 0
2018-03-19 | 1100 | [13 empty] | 0
2018-03-20 | 1411 | [13 empty] | 0
2018-03-21 | 1301 | [13 empty] | 0
2018-03-22 | 1301 | [13 empty] | 1
2018-03-23 | 1304 | [13 empty] | 1
2018-03-24 | 1647 | [13 empty] | 3
2018-03-25 | 998 | [13 empty] | 15
2018-03-26 | 1220 | 0.56 | <2 | 7.1 | 1 | 3 | 2 | 8.3 | 0.15 | 2.77 | 11.5 | 1.39 | 0.21 | 4.16 | 3 | 8.4 | 2018-04-13 | 2018-04-13
2018-03-27 | 1501 | [13 empty] | 0
2018-03-28 | 1297 | [13 empty] | 0
2018-03-29 | 1496 | [13 empty] | 3
2018-03-30 | 1823 | [13 empty] | 0
2018-03-31 | 1409 | [13 empty] | 7
2018-04-01 | 1426 | [13 empty] | 0
2018-04-02 | 1441 | [13 empty] | 0
2018-04-03 | 1421 | [13 empty] | 0
2018-04-04 | 1493 | [13 empty] | 0
2018-04-05 | 1259 | [13 empty] | 0
2018-04-06 | 1547 | [13 empty] | 4
2018-04-07 | 1183 | [13 empty] | 0
2018-04-08 | 1421 | [13 empty] | 0
2018-04-09 | 1480 | 0.46 | 1 | 7 | 1 | 5 | 2 | 5.7 | 0.09 | 2.96 | 8.44 | 1.48 | 0.13 | 7.4 | 0 | 10:45 | 2018-04-20 | 2018-04-20
2018-04-10 | 1207 | [13 empty] | 0
2018-04-11 | 1256 | [13 empty] | 0
2018-04-12 | 1291 | [13 empty] | 0
2018-04-13 | 1131 | [13 empty] | 0
2018-04-14 | 1485 | [13 empty] | 0
2018-04-15 | 1008 | [13 empty] | 0
2018-04-16 | 871 | [13 empty] | 0
2018-04-17 | 1696 | [13 empty] | 0
2018-04-18 | 670 | [13 empty] | 0
2018-04-19 | 2030 | [13 empty] | 14
2018-04-20 | 874 | [13 empty] | 2
2018-04-21 | 1478 | [13 empty] | 0
2018-04-22 | 1089 | [13 empty] | 1
2018-04-23 | 1612 | 0.47 | 1 | 7.2 | 1 | 5 | 2 | 6.6 | 0.13 | 3.22 | 10.64 | 1.61 | 0.21 | 8.06 | 18 | 15:45 | 2018-05-04 | 2018-05-04
2018-04-24 | 1394 | [13 empty] | 32
2018-04-25 | 1956 | [13 empty] | 10
2018-04-26 | 1909 | [13 empty] | 35
2018-04-27 | 1424 | [13 empty] | 0
2018-04-28 | 1715 | [13 empty] | 3
2018-04-29 | 1601 | [13 empty] | 2
2018-04-30 | 1404 | [13 empty] | 12
2018-05-01 | 2030 | [13 empty] | 14
2018-05-02 | 1687 | [13 empty] | 14
2018-05-03 | 2303 | [13 empty] | 0
2018-05-04 | 1341 | [13 empty] | 0
2018-05-05 | 1623 | [13 empty] | 0
2018-05-06 | 1343 | [13 empty] | 0
2018-05-07 | 1812 | 0.6 | 1 | 7.2 | 1 | 5 | 2 | 6.9 | 0.12 | 3.62 | 12.5 | 1.81 | 0.22 | 9.06 | 0 | 9:05 | 2018-05-18 | 2018-05-18
2018-05-08 | 1666 | [13 empty] | 1
2018-05-09 | 1581 | [13 empty] | 5
2018-05-10 | 1806 | [13 empty] | 16
2018-05-11 | 1529 | [13 empty] | 0
2018-05-12 | 1278 | [13 empty] | 0
2018-05-13 | 1671 | [13 empty] | 0
2018-05-14 | 1568 | [13 empty] | 0
2018-05-15 | 1447 | [13 empty] | 0
2018-05-16 | 1606 | [13 empty] | 0
2018-05-17 | 1164 | [13 empty] | 0
2018-05-18 | 1417 | [13 empty] | 3
2018-05-19 | 1214 | [13 empty] | 8
2018-05-20 | 1425 | [13 empty] | 0
2018-05-21 | 1575 | 0.63 | 2 | 7.3 | 1 | 1 | 2 | 5.7 | 0.09 | 3.15 | 8.98 | 3.15 | 0.14 | 1.58 | 0 | 10:25 | 2018-05-21 | 2018-05-21
2018-05-22 | 1143 | [13 empty] | 0
2018-05-23 | 1493 | [13 empty] | 0
2018-05-24 | 1190 | [13 empty] | 0
2018-05-25 | 1543 | [13 empty] | 2
2018-05-26 | 1159 | [13 empty] | 0
2018-05-27 | 1375 | [13 empty] | 12
2018-05-28 | 1323 | [13 empty] | 2
2018-05-29 | 1656 | [13 empty] | 10
2018-05-30 | 1331 | [13 empty] | 0
2018-05-31 | 1264 | [13 empty] | 0
MINIMUM | 644 | 0.12 | 1 | 6.8 | 1 | 1 | 1 | 2.5 | 0.06 | 1.21 | 4.61 | 1.21 | 0.02 | 1.58 | 0
AVERAGE | 1552.0027 | 0.6084 | 1.0417 | 7.0577 | 3.7619 | 4.6923 | 2.08 | 5.4731 | 0.12538 | 2.9931 | 8.8031 | 1.6865 | 0.20262 | 7.7677 | 4.0548
MAXIMUM | 7700 | 1.2 | 2 | 7.3 | 33 | 9 | 3 | 8.4 | 0.2 | 7.2 | 15.31 | 3.6 | 0.5 | 17.99 | 112
| Sample Count | 25 | [6 empty] | Total | 77.82 | 228.88 | 43.85 | 5.2681 | 201.96 | 1480

## 18-19
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 18/19
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | - | -
2018-06-01 | 1212 | [13 empty] | 0
2018-06-02 | 953 | [13 empty] | 0
2018-06-03 | 1436 | [13 empty] | 0
2018-06-04 | 1241 | [13 empty] | 0
2018-06-05 | 1021 | 0.47 | 2 | 7.1 | 2 | 5 | 2 | 4.7 | 0.1 | 2.04 | 4.8 | 2.04 | 0.1 | 5.11 | 1 | 9:50 AM | 2018-06-14 | 2018-06-14
2018-06-06 | 1544 | [13 empty] | 6
2018-06-07 | 1090 | [13 empty] | 6
2018-06-08 | 2226 | [13 empty] | 46
2018-06-09 | 1949 | [13 empty] | 2
2018-06-10 | 1463 | [13 empty] | 3
2018-06-11 | 1985 | [13 empty] | 6
2018-06-12 | 1420 | [13 empty] | 0
2018-06-13 | 1518 | [13 empty] | 0
2018-06-14 | 1648 | [13 empty] | 0
2018-06-15 | 1598 | [13 empty] | 0
2018-06-16 | 1428 | [13 empty] | 0
2018-06-17 | 1611 | [13 empty] | 0
2018-06-18 | 1804 | [13 empty] | 0
2018-06-19 | 1248 | 0.57 | <2 | 7 | 1 | 2 | <2 | 4.5 | 0.1 | 1.25 | 5.62 | 1.25 | 0.12 | 2.5 | 0 | 13:20 | 2018-06-27 | 2018-06-27
2018-06-20 | 1637 | [13 empty] | 0
2018-06-21 | 1222 | [13 empty] | 0
2018-06-22 | 1216 | [13 empty] | 1
2018-06-23 | 1462 | [13 empty] | 1
2018-06-24 | 1755 | [13 empty] | 0
2018-06-25 | 1549 | [13 empty] | 0
2018-06-26 | 1702 | [13 empty] | 0
2018-06-27 | 1018 | [13 empty] | 0
2018-06-28 | 1747 | [13 empty] | 5
2018-06-29 | 1555 | [13 empty] | 6
2018-06-30 | 1447 | [13 empty] | 0
2018-07-01 | 1339 | [13 empty] | 0
2018-07-02 | 1300 | [13 empty] | 0
2018-07-03 | 1071 | 0.4 | <2 | 7.1 | <10 | 2 | <2 | 5.1 | 0.08 | 1.07 | 5.46 | 1.07 | 0.09 | 2.14 | 2 | 9:05 | 2018-07-10 | 2018-07-10
2018-07-04 | 1873 | [13 empty] | 2
2018-07-05 | 1475 | [13 empty] | 16
2018-07-06 | 1662 | [13 empty] | 5
2018-07-07 | 1682 | [13 empty] | 8
2018-07-08 | 1193 | [13 empty] | 3
2018-07-09 | 1759 | [13 empty] | 0
2018-07-10 | 1314 | [13 empty] | 0
2018-07-11 | 1450 | [13 empty] | 0
2018-07-12 | 1635 | [13 empty] | 0
2018-07-13 | 1335 | [13 empty] | 2
2018-07-14 | 1401 | [13 empty] | 0
2018-07-15 | 1518 | [13 empty] | 0
2018-07-16 | 1396 | [13 empty] | 0
2018-07-17 | 1140 | 0.79 | 2 | 7.2 | 31 | 4 | 3 | 6.6 | 0.12 | 3.42 | 7.52 | 2.28 | 0.14 | 4.56 | 0 | 9:35 | 2018-07-26 | 2018-07-26
2018-07-18 | 1776 | [13 empty] | 0
2018-07-19 | 1186 | [13 empty] | 0
2018-07-20 | 1270 | [13 empty] | 0
2018-07-21 | 1337 | [13 empty] | 0
2018-07-22 | 1339 | [13 empty] | 0
2018-07-23 | 1120 | [13 empty] | 0
2018-07-24 | 1274 | [13 empty] | 0
2018-07-25 | 1616 | [13 empty] | 0
2018-07-26 | 1187 | [13 empty] | 0
2018-07-27 | 1067 | [13 empty] | 0
2018-07-28 | 1435 | [13 empty] | 0
2018-07-29 | 1253 | [13 empty] | 0
2018-07-30 | 1129 | [13 empty] | 1
2018-07-31 | 1219 | 0.38 | 2 | 7.1 | 3 | 2 | 2 | 5.7 | 0.11 | 2.44 | 6.95 | 2.44 | 0.13 | 2.44 | 0 | 10:45 | 2018-08-14 | 2018-08-14
2018-08-01 | 1551 | [13 empty] | 0
2018-08-02 | 896 | [13 empty] | 0
2018-08-03 | 1289 | [13 empty] | 0
2018-08-04 | 1487 | [13 empty] | 0
2018-08-05 | 989 | [13 empty] | 0
2018-08-06 | 1529 | [13 empty] | 0
2018-08-07 | 1138 | [13 empty] | 0
2018-08-08 | 666 | [13 empty] | 0
2018-08-09 | 1439 | [13 empty] | 0
2018-08-10 | 1303 | [13 empty] | 0
2018-08-11 | 942 | [13 empty] | 0
2018-08-12 | 1294 | [13 empty] | 0
2018-08-13 | 1207 | [13 empty] | 0
2018-08-14 | 1394 | 0.44 | 2 | 7.5 | 2 | 1 | 2 | 6.2 | 0.12 | 2.79 | 8.64 | 2.79 | 0.17 | 1.39 | 0 | 9:00 | 2018-08-22 | 2018-08-22
2018-08-15 | 1372 | [13 empty] | 0
2018-08-16 | 1043 | [13 empty] | 0
2018-08-17 | 1154 | [13 empty] | 0
2018-08-18 | 1346 | [13 empty] | 0
2018-08-19 | 1059 | [13 empty] | 0
2018-08-20 | 1268 | [13 empty] | 0
2018-08-21 | 1247 | [13 empty] | 0
2018-08-22 | 1182 | [13 empty] | 0
2018-08-23 | 1114 | [13 empty] | 0
2018-08-24 | 1212 | [13 empty] | 3
2018-08-25 | 872 | [13 empty] | 6
2018-08-26 | 1207 | [13 empty] | 5
2018-08-27 | 1235 | [13 empty] | 15
2018-08-28 | 1027 | 0.59 | 2 | 7.1 | 5 | 3 | 2 | 6.4 | 0.08 | 2.05 | 6.57 | 2.05 | 0.08 | 3.08 | 4 | 10:20 | 2018-09-13 | 2018-09-13
2018-08-29 | 1653 | [13 empty] | 0
2018-08-30 | 1019 | [13 empty] | 0
2018-08-31 | 1396 | [13 empty] | 0
2018-09-01 | 1213 | [13 empty] | 4
2018-09-02 | 1173 | [13 empty] | 0
2018-09-03 | 1189 | [13 empty] | 9
2018-09-04 | 1224 | [13 empty] | 30
2018-09-05 | 1448 | [13 empty] | 26
2018-09-06 | 1935 | [13 empty] | 13
2018-09-07 | 1441 | [13 empty] | 0
2018-09-08 | 1842 | [13 empty] | 0
2018-09-09 | 1241 | [13 empty] | 1
2018-09-10 | 1264 | [13 empty] | 0
2018-09-11 | 1260 | 0.98 | 2 | 7.4 | 10 | 6 | 2 | 5.4 | 0.23 | 2.52 | 6.8 | 2.52 | 0.29 | 7.56 | 0 | 9:25 | 2018-09-19 | 2018-09-19
2018-09-12 | 1228 | [13 empty] | 0
2018-09-13 | 1575 | [13 empty] | 0
2018-09-14 | 1386 | [13 empty] | 0
2018-09-15 | 1397 | [13 empty] | 0
2018-09-16 | 908 | [13 empty] | 0
2018-09-17 | 1416 | [13 empty] | 4
2018-09-18 | 1477 | [13 empty] | 0
2018-09-19 | 911 | [13 empty] | 0
2018-09-20 | 1429 | [13 empty] | 1
2018-09-21 | 1594 | [13 empty] | 10
2018-09-22 | 856 | [13 empty] | 0
2018-09-23 | 1420 | [13 empty] | 0
2018-09-24 | 1560 | [13 empty] | 0
2018-09-25 | 1111 | 0.54 | 2 | 7.3 | 10 | 5 | 2 | 4.4 | 0.11 | 2.22 | 4.89 | 2.22 | 0.12 | 5.56 | 7 | 9:55 | 2018-10-09 | 2018-10-09
2018-09-26 | 1162 | [13 empty] | 1
2018-09-27 | 1313 | [13 empty] | 2
2018-09-28 | 944 | [13 empty] | 0
2018-09-29 | 1305 | [13 empty] | 0
2018-09-30 | 1545 | [13 empty] | 2
2018-10-01 | 1105 | [13 empty] | 0
2018-10-02 | 1407 | [13 empty] | 0
2018-10-03 | 1143 | [13 empty] | 0
2018-10-04 | 1285 | [13 empty] | 0
2018-10-05 | 1486 | [13 empty] | 0
2018-10-06 | 1167 | [13 empty] | 2
2018-10-07 | 1019 | [13 empty] | 4
2018-10-08 | 1376 | [13 empty] | 0
2018-10-09 | 923 | 0.52 | 2 | 7.3 | 10 | 5 | 2 | 4 | 0.13 | 1.85 | 3.69 | 1.85 | 0.12 | 4.62 | 0 | 15:55 | 2018-10-22 | 2018-10-22
2018-10-10 | 1061 | [13 empty] | 0
2018-10-11 | 1565 | [13 empty] | 44
2018-10-12 | 1901 | [13 empty] | 28
2018-10-13 | 2167 | [13 empty] | 8
2018-10-14 | 2188 | [13 empty] | 36
2018-10-15 | 2560 | [13 empty] | 32
2018-10-16 | 3024 | [13 empty] | 7
2018-10-17 | 2639 | [13 empty] | 23
2018-10-18 | 2912 | [13 empty] | 1
2018-10-19 | 2099 | [13 empty] | 0
2018-10-20 | 1730 | [13 empty] | 0
2018-10-21 | 1572 | [13 empty] | 0
2018-10-22 | 1983 | [13 empty] | 22
2018-10-23 | 1598 | 0.66 | 1 | 7.1 | 80 | 3 | 2 | 3.6 | 0.13 | 3.2 | 5.75 | 1.6 | 0.21 | 4.79 | 0 | 11:35 | 2018-11-06 | 2018-11-06
2018-10-24 | 1816 | [13 empty] | 0
2018-10-25 | 1435 | [13 empty] | 0
2018-10-26 | 1263 | [13 empty] | 0
2018-10-27 | 1811 | [13 empty] | 0
2018-10-28 | 1563 | [13 empty] | 0
2018-10-29 | 1389 | [13 empty] | 0
2018-10-30 | 1215 | [13 empty] | 2
2018-10-31 | 1192 | [13 empty] | 0
2018-11-01 | 1593 | [13 empty] | 0
2018-11-02 | 1192 | [13 empty] | 0
2018-11-03 | 1237 | [13 empty] | 0
2018-11-04 | 1571 | [13 empty] | 0
2018-11-05 | 1333 | [13 empty] | 0
2018-11-06 | 1420 | 0.41 | 1 | 7.2 | 10 | 5 | 2 | 4.2 | 0.09 | 2.84 | 5.96 | 1.42 | 0.13 | 7.1 | 0 | 10:25 | 2018-11-16 | 2018-11-16
2018-11-07 | 1235 | [13 empty] | 0
2018-11-08 | 846 | [13 empty] | 3
2018-11-09 | 1739 | [13 empty] | 1
2018-11-10 | 1270 | [13 empty] | 0
2018-11-11 | 1212 | [13 empty] | 19
2018-11-12 | 1901 | [13 empty] | 0
2018-11-13 | 1371 | [13 empty] | 0
2018-11-14 | 1449 | [13 empty] | 0
2018-11-15 | 1165 | [13 empty] | 0
2018-11-16 | 1136 | [13 empty] | 0
2018-11-17 | 1467 | [13 empty] | 3
2018-11-18 | 1239 | [13 empty] | 6
2018-11-19 | 1319 | [13 empty] | 1
2018-11-20 | 1326 | 0.83 | 2 | 7 | 13 | 5 | 2 | 4.5 | 0.14 | 2.65 | 5.97 | 2.65 | 0.19 | 6.63 | 0 | 9:50 | 2018-11-28 | 2018-11-28
2018-11-21 | 1018 | [13 empty] | 0
2018-11-22 | 1405 | [13 empty] | 5
2018-11-23 | 1366 | [13 empty] | 12
2018-11-24 | 1880 | [13 empty] | 0
2018-11-25 | 974 | [13 empty] | 0
2018-11-26 | 1470 | [13 empty] | 0
2018-11-27 | 1260 | [13 empty] | 0
2018-11-28 | 1223 | [13 empty] | 7
2018-11-29 | 1149 | [13 empty] | 3
2018-11-30 | 1163 | [13 empty] | 0
2018-12-01 | 1219 | [13 empty] | 0
2018-12-02 | 1119 | [13 empty] | 0
2018-12-03 | 1155 | [13 empty] | 0
2018-12-04 | 1212 | 0.54 | 2 | 7.1 | 10 | 5 | 2 | 4.4 | 0.12 | 2.42 | 5.33 | 2.42 | 0.15 | 6.06 | 0 | 10:00 | 2018-12-11 | 2018-12-11
2018-12-05 | 968 | [13 empty] | 0
2018-12-06 | 1425 | [13 empty] | 0
2018-12-07 | 727 | [13 empty] | 0
2018-12-08 | 1467 | [13 empty] | 0
2018-12-09 | 1182 | [13 empty] | 0
2018-12-10 | 953 | [13 empty] | 0
2018-12-11 | 1451 | [13 empty] | 0
2018-12-12 | 1138 | [13 empty] | 0
2018-12-13 | 1074 | [13 empty] | 0
2018-12-14 | 1190 | [13 empty] | 0
2018-12-15 | 1243 | [13 empty] | 0
2018-12-16 | 1112 | [13 empty] | 1
2018-12-17 | 1336 | [13 empty] | 2
2018-12-18 | 965 | 0.53 | 2 | 7 |  | 2 | 2 | 5.3 | 0.12 | 1.93 | 5.11 | 1.93 | 0.12 | 1.93 | 9 | 10:45 | 2018-12-21 | 2018-12-21
2018-12-19 | 1370 | [13 empty] | 0
2018-12-20 | 1486 | [13 empty] | 4
2018-12-21 | 765 | [13 empty] | 7
2018-12-22 | 1640 | [13 empty] | 18
2018-12-23 | 1398 | [13 empty] | 10
2018-12-24 | 1256 | [13 empty] | 1
2018-12-25 | 1548 | [13 empty] | 0
2018-12-26 | 1184 | [13 empty] | 0
2018-12-27 | 1445 | [13 empty] | 0
2018-12-28 | 1571 | [13 empty] | 0
2018-12-29 | 1351 | [13 empty] | 0
2018-12-30 | 1308 | [13 empty] | 0
2018-12-31 | 1592 | [13 empty] | 0
2019-01-01 | 1530 | 1.1 | 1 | 7.2 | 10 | 1 | 2 | 6.8 | 0.18 | 3.06 | 10.4 | 1.53 | 0.28 | 1.53 | 0 | 9:50 | 2019-01-14 | 2019-01-14
2019-01-02 | 1217 | [13 empty] | 0
2019-01-03 | 1633 | [13 empty] | 0
2019-01-04 | 1414 | [13 empty] | 0
2019-01-05 | 1765 | [13 empty] | 0
2019-01-06 | 1272 | [13 empty] | 0
2019-01-07 | 1285 | [13 empty] | 0
2019-01-08 | 1455 | [13 empty] | 0
2019-01-09 | 1511 | [13 empty] | 0
2019-01-10 | 1349 | [13 empty] | 0
2019-01-11 | 1196 | [13 empty] | 0
2019-01-12 | 1404 | [13 empty] | 0
2019-01-13 | 1188 | [13 empty] | 0
2019-01-14 | 1347 | [13 empty] | 0
2019-01-15 | 1130 | 1.1 | 2 | 7.1 | 1 | 2 | 2 | 5.3 | 0.21 | 2.26 | 5.99 | 2.26 | 0.24 | 2.26 | 0 | 9:05 | 2019-01-15 | 2019-01-15
2019-01-16 | 1272 | [13 empty] | 0
2019-01-17 | 1601 | [13 empty] | 0
2019-01-18 | 1285 | [13 empty] | 0
2019-01-19 | 1120 | [13 empty] | 0
2019-01-20 | 1413 | [13 empty] | 0
2019-01-21 | 1056 | [13 empty] | 0
2019-01-22 | 1399 | [13 empty] | 0
2019-01-23 | 1093 | [13 empty] | 0
2019-01-24 | 942 | [13 empty] | 2
2019-01-25 | 1519 | [13 empty] | 0
2019-01-26 | 870 | [13 empty] | 0
2019-01-27 | 1396 | [13 empty] | 0
2019-01-28 | 242 | [13 empty] | 0
2019-01-29 | 516 | 0.63 | 1 | 7.2 | 27 | 13 | 2 | 7.6 | 0.4 | 1.03 | 3.92 | 0.52 | 0.21 | 6.71 | 0 | 7:30 | 2019-02-15 | 2019-02-15
2019-01-30 | 950 | [13 empty] | 0
2019-01-31 | 1086 | [13 empty] | 0
2019-02-01 | 1167 | [13 empty] | 0
2019-02-02 | 1374 | [13 empty] | 13
2019-02-03 | 1401 | [13 empty] | 0
2019-02-04 | 663 | [13 empty] | 2
2019-02-05 | 1378 | [13 empty] | 0
2019-02-06 | 1561 | [13 empty] | 0
2019-02-07 | 1195 | [13 empty] | 0
2019-02-08 | 1043 | [13 empty] | 0
2019-02-09 | 1058 | [13 empty] | 0
2019-02-10 | 1174 | [13 empty] | 0
2019-02-11 | 1033 | [13 empty] | 0
2019-02-12 | 1183 | 0.24 | 1 | 7.2 | 1 | 9 | 2 | 5.6 | 0.12 | 2.37 | 6.62 | 1.18 | 0.14 | 10.65 | 0 | 11:55 | 2019-02-19 | 2019-02-19
2019-02-13 | 1069 | [13 empty] | 0
2019-02-14 | 813 | [13 empty] | 0
2019-02-15 | 1373 | [13 empty] | 0
2019-02-16 | 1104 | [13 empty] | 0
2019-02-17 | 983 | [13 empty] | 0
2019-02-18 | 1363 | [13 empty] | 0
2019-02-19 | 795 | [13 empty] | 0
2019-02-20 | 1233 | [13 empty] | 0
2019-02-21 | 1010 | [13 empty] | 0
2019-02-22 | 992 | [13 empty] | 5
2019-02-23 | 911 | [13 empty] | 9
2019-02-24 | 1381 | [13 empty] | 10
2019-02-25 | 965 | [13 empty] | 3
2019-02-26 | 1055 | 0.43 | 1 | 7.3 | <1 | 5 | <2 | 6.1 | 0.15 | 2.11 | 6.44 | 1.06 | 0.16 | 5.28 | 1 | 10:00 | 2019-03-08 | 2019-03-08
2019-02-27 | 1153 | [13 empty] | 0
2019-02-28 | 948 | [13 empty] | 0
2019-03-01 | 548 | [13 empty] | 0
2019-03-02 | 1509 | [13 empty] | 1
2019-03-03 | 983 | [13 empty] | 8
2019-03-04 | 1344 | [13 empty] | 1
2019-03-05 | 1009 | [13 empty] | 0
2019-03-06 | 1060 | [13 empty] | 2
2019-03-07 | 1111 | [13 empty] | 0
2019-03-08 | 952 | [13 empty] | 8
2019-03-09 | 1361 | [13 empty] | 0
2019-03-10 | 959 | [13 empty] | 0
2019-03-11 | 959 | [13 empty] | 0
2019-03-12 | 1285 | 49 | 1 | 7.1 | 2 | 6 | 2 | 5.9 | 0.11 | 2.57 | 7.58 | 1.29 | 0.14 | 7.71 | 0 | 8:45 | 2019-03-12 | 2019-03-12
2019-03-13 | 1058 | [13 empty] | 0
2019-03-14 | 1044 | [13 empty] | 0
2019-03-15 | 1076 | [13 empty] | 3
2019-03-16 | 892 | [13 empty] | 19
2019-03-17 | 1148 | [13 empty] | 23
2019-03-18 | 1006 | [13 empty] | 9
2019-03-19 | 1313 | [13 empty] | 0
2019-03-20 | 1309 | [13 empty] | 0
2019-03-21 | 1000 | [13 empty] | 0
2019-03-22 | 967 | [13 empty] | 0
2019-03-23 | 1497 | [13 empty] | 1
2019-03-24 | 1273 | [13 empty] | 0
2019-03-25 | 872 | [13 empty] | 0
2019-03-26 | 1235 | 0.34 | 1 | 7.1 | 1 | 5 | 2 | 5.7 | 0.13 | 2.47 | 7.04 | 1.24 | 0.16 | 6.18 | 0 | 15:45 | 2019-04-12 | 2019-04-12
2019-03-27 | 1183 | [13 empty] | 12
2019-03-28 | 1055 | [13 empty] | 9
2019-03-29 | 1291 | [13 empty] | 2
2019-03-30 | 1147 | [13 empty] | 1
2019-03-31 | 1112 | [13 empty] | 2
2019-04-01 | 575 | [13 empty] | 0
2019-04-02 | 1621 | [13 empty] | 1
2019-04-03 | 1615 | [13 empty] | 35
2019-04-04 | 1641 | [13 empty] | 1
2019-04-05 | 628 | [13 empty] | 0
2019-04-06 | 1709 | [13 empty] | 0
2019-04-07 | 968 | [13 empty] | 0
2019-04-08 | 1375 | [13 empty] | 0
2019-04-09 | 1111 | 0.55 | 1 | 7.1 | 1 | 2 | 1 | 4.4 | 0.13 | 1.11 | 4.89 | 1.11 | 0.14 | 2.22 | 0 | 10:55 | 2019-04-30 | 2019-04-30
2019-04-10 | 1274 | [13 empty] | 3
2019-04-11 | 1074 | [13 empty] | 10
2019-04-12 | 1051 | [13 empty] | 12
2019-04-13 | 1051 | [13 empty] | 5
2019-04-14 | 1197 | [13 empty] | 1
2019-04-15 | 1460 | [13 empty] | 3
2019-04-16 | 963 | [13 empty] | 21
2019-04-17 | 1225 | [13 empty] | 7
2019-04-18 | 1684 | [13 empty] | 6
2019-04-19 | 1127 | [13 empty] | 2
2019-04-20 | 1571 | [13 empty] | 9
2019-04-21 | 1656 | [13 empty] | 1
2019-04-22 | 1739 | [13 empty] | 1
2019-04-23 | 1319 | 0.96 | 1 | 7.2 | 1 | 2 | 1 | 7.8 | 0.15 | 1.32 | 10.29 | 1.32 | 0.2 | 2.64 | 0 | 6:30 | 2019-05-03 | 2019-05-09
2019-04-24 | 1564 | [13 empty] | 0
2019-04-25 | 1384 | [13 empty] | 0
2019-04-26 | 1244 | [13 empty] | 0
2019-04-27 | 1315 | [13 empty] | 0
2019-04-28 | 1399 | [13 empty] | 0
2019-04-29 | 1242 | [13 empty] | 0
2019-04-30 | 1086 | [13 empty] | 1
2019-05-01 | 1445 | [13 empty] | 5
2019-05-02 | 505 | [13 empty] | 9
2019-05-03 | 1755 | [13 empty] | 0
2019-05-04 | 997 | [13 empty] | 0
2019-05-05 | 1275 | [13 empty] | 2
2019-05-06 | 1074 | [13 empty] | 0
2019-05-07 | 1484 | 0.72 | 1 | 7.3 | 3 | 4 | 2 | 7.5 | 0.09 | 2.97 | 11.13 | 1.48 | 0.13 | 5.94 | 0 | 9:35 | 2019-05-17 | 2019-05-22
2019-05-08 | 931 | [13 empty] | 0
2019-05-09 | 1717 | [13 empty] | 0
2019-05-10 | 675 | [13 empty] | 2
2019-05-11 | 1597 | [13 empty] | 0
2019-05-12 | 982 | [13 empty] | 0
2019-05-13 | 794 | [13 empty] | 6
2019-05-14 | 1579 | [13 empty] | 2
2019-05-15 | 468 | [13 empty] | 0
2019-05-16 | 1726 | [13 empty] | 3
2019-05-17 | 1726 | [13 empty] | 3
2019-05-18 | 1126 | [13 empty] | 1
2019-05-19 | 1171 | [13 empty] | 6
2019-05-20 | 614 | [13 empty] | 2
2019-05-21 | 1489 | 0.39 | 1 | 7.2 | 1 | 3 | 1 | 4.8 | 0.1 | 1.49 | 7.15 | 1.49 | 0.15 | 4.47 | 0 | 9:15 | 2019-05-28 | 2019-05-28
2019-05-22 | 1333 | [13 empty] | 0
2019-05-23 | 1333 | [13 empty] | 3
2019-05-24 | 918 | [13 empty] | 2
2019-05-25 | 1115 | [13 empty] | 0
2019-05-26 | 1445 | [13 empty] | 0
2019-05-27 | 1152 | [13 empty] | 0
2019-05-28 | 972 | [13 empty] | 0
2019-05-29 | 930 | [13 empty] | 0
2019-05-30 | 1459 | [13 empty] | 0
2019-05-31 | 1091 | [13 empty] | 0
MINIMUM | 242 | 0.24 | 1 | 7 | 1 | 1 | 1 | 3.6 | 0.08 | 1.03 | 3.69 | 0.52 | 0.08 | 1.39 | 0
AVERAGE | 1302.0932 | 2.4658 | 1.5 | 7.1731 | 10.2174 | 4.1154 | 1.913 | 5.4808 | 0.13654 | 2.2096 | 6.5581 | 1.7312 | 0.15808 | 4.6562 | 2.4575
MAXIMUM | 3024 | 49 | 2 | 7.5 | 80 | 13 | 3 | 7.8 | 0.4 | 3.42 | 11.13 | 2.79 | 0.29 | 10.65 | 46
| Sample Count | 26 | [6 empty] | Total | 57.45 | 170.51 | 45.01 | 4.11 | 121.06 | 897

## 19-20
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 19/20
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | - | -
2019-06-01 | 1672 | [13 empty] | 0
2019-06-02 | 1088 | [13 empty] | 15
2019-06-03 | 1158 | [13 empty] | 4
2019-06-04 | 1052 | 0.69 | <2 | 7.3 | <1 | 5 | 2 | 5.6 | 0.13 | 2.1 | 5.89 | 1.05 | 0.14 | 5.26 | 0 | 9:45 | 2019-06-17 | 2019-06-17
2019-06-05 | 1031 | [13 empty] | 0
2019-06-06 | 516 | [13 empty] | 0
2019-06-07 | 1671 | [13 empty] | 0
2019-06-08 | 1175 | [13 empty] | 4
2019-06-09 | 787 | [13 empty] | 17
2019-06-10 | 1414 | [13 empty] | 0
2019-06-11 | 1214 | [13 empty] | 0
2019-06-12 | 1094 | [13 empty] | 0
2019-06-13 | 1177 | [13 empty] | 0
2019-06-14 | 1261 | [13 empty] | 0
2019-06-15 | 885 | [13 empty] | 3
2019-06-16 | 1232 | [13 empty] | 1
2019-06-17 | 758 | [13 empty] | 3
2019-06-18 | 1406 | 0.77 | 2 | 7 | 1 | 4 | 2 | 5.8 | 0.18 | 2.81 | 8.15 | 2.81 | 0.25 | 5.62 | 0 | 10:25 | 2019-06-26 | 2019-06-26
2019-06-19 | 1267 | [13 empty] | 2
2019-06-20 | 537 | [13 empty] | 0
2019-06-21 | 1278 | [13 empty] | 1
2019-06-22 | 1595 | [13 empty] | 0
2019-06-23 | 979 | [13 empty] | 0
2019-06-24 | 894 | [13 empty] | 2
2019-06-25 | 2247 | [13 empty] | 77
2019-06-26 | 2512 | [13 empty] | 19
2019-06-27 | 1858 | [13 empty] | 26
2019-06-28 | 1925 | [13 empty] | 18
2019-06-29 | 2396 | [13 empty] | 2
2019-06-30 | 1790 | [13 empty] | 6
2019-07-01 | 2265 | [13 empty] | 4
2019-07-02 | 1572 | 0.55 | 2 | 7.1 | 1 | 3 | 2 | 4.4 | 0.14 | 3.14 | 6.92 | 3.14 | 0.22 | 4.72 | 0 | 11:45 | 2019-07-15 | 2019-07-24
2019-07-03 | 2269 | [13 empty] | 0
2019-07-04 | 1880 | [13 empty] | 8
2019-07-05 | 1634 | [13 empty] | 2
2019-07-06 | 1774 | [13 empty] | 3
2019-07-07 | 2106 | [13 empty] | 3
2019-07-08 | 1891 | [13 empty] | 12
2019-07-09 | 1580 | [13 empty] | 1
2019-07-10 | 1996 | [13 empty] | 0
2019-07-11 | 1415 | [13 empty] | 0
2019-07-12 | 1285 | [13 empty] | 0
2019-07-13 | 1647 | [13 empty] | 0
2019-07-14 | 1304 | [13 empty] | 0
2019-07-15 | 1669 | [13 empty] | 0
2019-07-16 | 1200 | 0.85 | 1 | 7.2 | 1 | 5 | 1 | 5.5 | 0.14 | 1.2 | 6.6 | 1.2 | 0.17 | 6 | 0 | 9:00 | 2019-07-26 | 2019-07-26
2019-07-17 | 1464 | [13 empty] | 0
2019-07-18 | 1740 | [13 empty] | 0
2019-07-19 | 1285 | [13 empty] | 0
2019-07-20 | 1361 | [13 empty] | 0
2019-07-21 | 1596 | [13 empty] | 0
2019-07-22 | 1159 | [13 empty] | 0
2019-07-23 | 1231 | [13 empty] | 0
2019-07-24 | 1804 | [13 empty] | 0
2019-07-25 | 994 | [13 empty] | 0
2019-07-26 | 1431 | [13 empty] | 1
2019-07-27 | 1085 | [13 empty] | 0
2019-07-28 | 1305 | [13 empty] | 0
2019-07-29 | 1295 | [13 empty] | 1
2019-07-30 | 1222 | 0.53 | 1 | 7.3 | 2 | 5 | 1 | 3.8 | 0.14 | 1.22 | 4.64 | 1.22 | 0.17 | 6.11 | 0 | 9:55 | 2019-08-08 | 2019-08-08
2019-07-31 | 1448 | [13 empty] | 6
2019-08-01 | 1198 | [13 empty] | 24
2019-08-02 | 1667 | [13 empty] | 3
2019-08-03 | 1299 | [13 empty] | 3
2019-08-04 | 1432 | [13 empty] | 0
2019-08-05 | 1150 | [13 empty] | 0
2019-08-06 | 1419 | [13 empty] | 0
2019-08-07 | 1132 | [13 empty] | 0
2019-08-08 | 1578 | [13 empty] | 0
2019-08-09 | 1547 | [13 empty] | 0
2019-08-10 | 847 | [13 empty] | 0
2019-08-11 | 1474 | [13 empty] | 0
2019-08-12 | 830 | [13 empty] | 0
2019-08-13 | 1788 | 0.74 | 1 | 7.3 | 1 | 5 | 2 | 6.3 | 0.19 | 1.22 | 11.26 | 1.22 | 0.34 | 8.94 | 0 | 10:00 | 2019-08-26 | 2019-09-03
2019-08-14 | 1225 | [13 empty] | 0
2019-08-15 | 1151 | [13 empty] | 0
2019-08-16 | 1165 | [13 empty] | 0
2019-08-17 | 1065 | [13 empty] | 0
2019-08-18 | 1022 | [13 empty] | 0
2019-08-19 | 1243 | [13 empty] | 0
2019-08-20 | 1291 | [13 empty] | 0
2019-08-21 | 880 | [13 empty] | 0
2019-08-22 | 1134 | [13 empty] | 0
2019-08-23 | 1843 | [13 empty] | 0
2019-08-24 | 1201 | [13 empty] | 0
2019-08-25 | 1072 | [13 empty] | 0
2019-08-26 | 1034 | [13 empty] | 0
2019-08-27 | 1365 | 0.76 | 1 | 7.3 | 2 | 4 | 2 | 4.3 | 0.11 | 2.73 | 5.87 | 1.37 | 0.15 | 5.46 | 0 | 16:00 | 2019-09-12 | 2019-09-17
2019-08-28 | 1203 | [13 empty] | 0
2019-08-29 | 1155 | [13 empty] | 0
2019-08-30 | 1140 | [13 empty] | 2
2019-08-31 | 590 | [13 empty] | 4
2019-09-01 | 1669 | [13 empty] | 0
2019-09-02 | 1341 | [13 empty] | 0
2019-09-03 | 1205 | [13 empty] | 0
2019-09-04 | 1128 | [13 empty] | 0
2019-09-05 | 1322 | [13 empty] | 0
2019-09-06 | 1174 | [13 empty] | 0
2019-09-07 | 864 | [13 empty] | 0
2019-09-08 | 1177 | [13 empty] | 0
2019-09-09 | 1351 | [13 empty] | 0
2019-09-10 | 990 | 0.62 | 1 | 7.3 | 5 | 5 | 2 | 4.7 | 0.14 | 1.98 | 4.65 | 0.99 | 0.14 | 4.95 | 0 | 8:55 | 2019-09-19 | 2019-09-30
2019-09-11 | 1164 | [13 empty] | 0
2019-09-12 | 1164 | [13 empty] | 0
2019-09-13 | 1102 | [13 empty] | 0
2019-09-14 | 1054 | [13 empty] | 0
2019-09-15 | 995 | [13 empty] | 0
2019-09-16 | 1191 | [13 empty] | 0
2019-09-17 | 1455 | [13 empty] | 0
2019-09-18 | 959 | [13 empty] | 1
2019-09-19 | 1284 | [13 empty] | 0
2019-09-20 | 1073 | [13 empty] | 0
2019-09-21 | 724 | [13 empty] | 1
2019-09-22 | 1271 | [13 empty] | 0
2019-09-23 | 850 | [13 empty] | 0
2019-09-24 | 1582 | 0.81 | 1 | 7.3 | 6 | 6 | 1 | 5.6 | 0.16 | 1.58 | 4.65 | 1.58 | 0.25 | 9.49 | 0 | 9:55 | 2019-10-09 | 2019-10-09
2019-09-25 | 1252 | [13 empty] | 0
2019-09-26 | 1150 | [13 empty] | 0
2019-09-27 | 885 | [13 empty] | 2
2019-09-28 | 1221 | [13 empty] | 2
2019-09-29 | 1555 | [13 empty] | 0
2019-09-30 | 886 | [13 empty] | 0
2019-10-01 | 1348 | [13 empty] | 0
2019-10-02 | 1118 | [13 empty] | 0
2019-10-03 | 686 | [13 empty] | 0
2019-10-04 | 1599 | [13 empty] | 0
2019-10-05 | 1206 | [13 empty] | 0
2019-10-06 | 1206 | [13 empty] | 0
2019-10-07 | 1206 | [13 empty] | 0
2019-10-08 | 1027 | 0.69 | 1 | 7.5 | 1 | 5 | 1 | 5.9 | 0.27 | 1.03 | 6.06 | 1.03 | 0.28 | 5.14 | 0 | 10:30 | 2019-10-28 | 2019-10-30
2019-10-09 | 1352 | [13 empty] | 0
2019-10-10 | 783 | [13 empty] | 1
2019-10-11 | 998 | [13 empty] | 0
2019-10-12 | 694 | [13 empty] | 13
2019-10-13 | 1515 | [13 empty] | 10
2019-10-14 | 890 | [13 empty] | 0
2019-10-15 | 1457 | [13 empty] | 0
2019-10-16 | 1078 | [13 empty] | 0
2019-10-17 | 1177 | [13 empty] | 1
2019-10-18 | 537 | [13 empty] | 2
2019-10-19 | 1566 | [13 empty] | 0
2019-10-20 | 1157 | [13 empty] | 0
2019-10-21 | 1012 | [13 empty] | 0
2019-10-22 | 743 | 0.37 | 1 | 7.3 | 1 | 3 | 2 | 5 | 0.24 | 1.03 | 3.72 | 0.74 | 0.18 | 2.23 | 0 | 13:30 | 2019-11-07 | 2019-11-13
2019-10-23 | 1396 | [13 empty] | 0
2019-10-24 | 1136 | [13 empty] | 0
2019-10-25 | 635 | [13 empty] | 0
2019-10-26 | 1446 | [13 empty] | 0
2019-10-27 | 895 | [13 empty] | 0
2019-10-28 | 1016 | [13 empty] | 0
2019-10-29 | 1304 | [13 empty] | 0
2019-10-30 | 724 | [13 empty] | 0
2019-10-31 | 946 | [13 empty] | 0
2019-11-01 | 1386 | [13 empty] | 0
2019-11-02 | 1077 | [13 empty] | 1
2019-11-03 | 1137 | [13 empty] | 0
2019-11-04 | 955 | [13 empty] | 0
2019-11-05 | 1132 | 0.44 | 1 | 7.6 | 1 | 9 | 3 | 4.6 | 0.21 | 3.4 | 5.21 | 1.13 | 0.24 | 10.19 | 0 | 13:45 | 2019-11-18 | 2019-11-27
2019-11-06 | 1045 | [13 empty] | 5
2019-11-07 | 1018 | [13 empty] | 0
2019-11-08 | 996 | [13 empty] | 0
2019-11-09 | 506 | [13 empty] | 0
2019-11-10 | 1569 | [13 empty] | 0
2019-11-11 | 732 | [13 empty] | 0
2019-11-12 | 1230 | [13 empty] | 0
2019-11-13 | 949 | [13 empty] | 0
2019-11-14 | 902 | [13 empty] | 0
2019-11-15 | 940 | [13 empty] | 0
2019-11-16 | 1329 | [13 empty] | 0
2019-11-17 | 855 | [13 empty] | 0
2019-11-18 | 1213 | [13 empty] | 0
2019-11-19 | 928 | 0.71 | 1 | 7.2 | <1 | 4 | 1 | 5.4 | 0.23 | 0.93 | 5.01 | 0.93 | 0.21 | 3.71 | 0 | 13:20 | 2019-12-02 | 2019-12-11
2019-11-20 | 765 | [13 empty] | 0
2019-11-21 | 1358 | [13 empty] | 0
2019-11-22 | 656 | [13 empty] | 0
2019-11-23 | 1260 | [13 empty] | 0
2019-11-24 | 1129 | [13 empty] | 0
2019-11-25 | 1278 | [13 empty] | 0
2019-11-26 | 1423 | [13 empty] | 0
2019-11-27 | 877 | [13 empty] | 0
2019-11-28 | 1275 | [13 empty] | 0
2019-11-29 | 767 | [13 empty] | 0
2019-11-30 | 1201 | [13 empty] | 0
2019-12-01 | 200 | [13 empty] | 6
2019-12-02 | 81 | [13 empty] | 11
2019-12-03 | 1025 | 0.71 | 1 | 7.5 | 3 | 3 | 2 | 3.5 | 0.18 | 2.05 | 3.59 | 1.03 | 0.18 | 3.08 | 0 | 8:35 | 2019-12-23 | 2019-12-23
2019-12-04 | 889 | [13 empty] | 0
2019-12-05 | 974 | [13 empty] | 0
2019-12-06 | 1052 | [13 empty] | 0
2019-12-07 | 1273 | [13 empty] | 0
2019-12-08 | 881 | [13 empty] | 0
2019-12-09 | 975 | [13 empty] | 0
2019-12-10 | 930 | [13 empty] | 0
2019-12-11 | 908 | [13 empty] | 2
2019-12-12 | 1027 | [13 empty] | 3
2019-12-13 | 1355 | [13 empty] | 0
2019-12-14 | 1054 | [13 empty] | 3
2019-12-15 | 937 | [13 empty] | 0
2019-12-16 | 1191 | [13 empty] | 0
2019-12-17 | 1365 | 0.5 | 1 | 7.4 | <1 | 4 | 2 | 3.3 | 0.16 | 2.73 | 4.5 | 1.37 | 0.22 | 5.46 | 0 | 11:00 | 2019-12-23 | 2019-12-30
2019-12-18 | 1504 | [13 empty] | 0
2019-12-19 | 1182 | [13 empty] | 0
2019-12-20 | 1114 | [13 empty] | 0
2019-12-21 | 855 | [13 empty] | 0
2019-12-22 | 1150 | [13 empty] | 0
2019-12-23 | 1508 | [13 empty] | 0
2019-12-24 | 768 | [13 empty] | 15
2019-12-25 | 1547 | [13 empty] | 0
2019-12-26 | 1043 | [13 empty] | 16
2019-12-27 | 1342 | [13 empty] | 0
2019-12-28 | 1302 | [13 empty] | 0
2019-12-29 | 1282 | [13 empty] | 0
2019-12-30 | 1373 | [13 empty] | 0
2019-12-31 | 1211 | [13 empty] | 0
2020-01-01 | 1091 | [13 empty] | 0
2020-01-02 | 1822 | [13 empty] | 0
2020-01-03 | 1303 | [13 empty] | 0
2020-01-04 | 750 | [13 empty] | 0
2020-01-05 | 1629 | [13 empty] | 0
2020-01-06 | 1343 | 1.6 | 1 | 7.3 | 1 | 4 | 6 | 3.9 | 0.33 | 8.06 | 5.24 | 1.34 | 0.44 | 5.37 | 0 | 10:30 | 2020-01-15 | 2020-01-15
2020-01-07 | 1098 | [13 empty] | 0
2020-01-08 | 1271 | [13 empty] | 0
2020-01-09 | 782 | [13 empty] | 0
2020-01-10 | 1390 | [13 empty] | 0
2020-01-11 | 1258 | [13 empty] | 0
2020-01-12 | 1257 | [13 empty] | 10
2020-01-13 | 957 | [13 empty] | 0
2020-01-14 | 1147 | [13 empty] | 0
2020-01-15 | 639 | [13 empty] | 0
2020-01-16 | 1533 | [13 empty] | 0
2020-01-17 | 690 | [13 empty] | 4
2020-01-18 | 1642 | [13 empty] | 40
2020-01-19 | 1756 | [13 empty] | 76
2020-01-20 | 1452 | 1.2 | 1 | 7.3 | 5 | 36 | 7 | 4.5 | 1.4 | 10.16 | 6.32 | 1.45 | 2.03 | 52.27 | 0 | 8:00 | 2020-01-31 | 2020-02-03 | → Following 116mm of rainfall over 18 & 19 January, activated sludge carried over from the Intermittent Decant Extended Aeration Tank (IDEAT) to the Catch Balance tanks. This carry over elevated both Total Suspended Solids (TSS) and Total Phosphorus (TP) above 100 percentile licence limits. The exceedance of licence limits was detected in laboratory samples collected 8.00am 20 January. While Council on-site testing conducted after 12.00pm 20 January indicates TP was back below the 100 percentile limit of 1.00mg/L.
2020-01-20 | 1452 | 1.3 | 1 | 7.55 | 5 | 7 | 3 | 2.91 | 0.38 | 4.36 | 4.23 | 1.45 | 0.45 | 8.2 | 0 | 12:00 | 2020-02-11 | 2020-02-11
2020-01-21 | 1276 | [13 empty] | 1
2020-01-22 | 1150 | [13 empty] | 0
2020-01-23 | 986 | [13 empty] | 0
2020-01-24 | 1810 | [13 empty] | 0
2020-01-25 | 1404 | [13 empty] | 0
2020-01-26 | 1331 | [13 empty] | 8
2020-01-27 | 1405 | [13 empty] | 0
2020-01-28 | 1172 | [13 empty] | 0
2020-01-29 | 1254 | [13 empty] | 0
2020-01-30 | 1546 | [13 empty] | 0
2020-01-31 | 855 | [13 empty] | 0
2020-02-01 | 1493 | [13 empty] | 0
2020-02-02 | 1156 | [13 empty] | 0
2020-02-03 | 1354 | 0.75 | 1 | 7.2 | 1 | 3 | 1 | 4.5 | 0.23 | 1.35 | 6.09 | 1.35 | 0.31 | 4.06 | 0 | 10:00 | 2020-02-18 | 2020-02-24
2020-02-04 | 1427 | [13 empty] | 16
2020-02-05 | 1307 | [13 empty] | 2
2020-02-06 | 1300 | [13 empty] | 3
2020-02-07 | 1838 | [13 empty] | 178
2020-02-08 | 5105 | [13 empty] | 21
2020-02-09 | 3161 | [13 empty] | 73
2020-02-10 | 5572 | [13 empty] | 34
2020-02-11 | 3081 | [13 empty] | 0
2020-02-12 | 2508 | [13 empty] | 0
2020-02-13 | 2873 | [13 empty] | 30
2020-02-14 | 4254 | [13 empty] | 22
2020-02-15 | 3455 | [13 empty] | 0
2020-02-16 | 2894 | [13 empty] | 0
2020-02-17 | 2485 | 0.36 | 1 | 7.1 | 3 | 9 | 1 | 6.7 | 0.23 | 2.49 | 16.65 | 2.49 | 0.57 | 22.37 | 0 | 11:15 | 2020-02-24 | 2020-03-10
2020-02-18 | 2675 | [13 empty] | 31
2020-02-19 | 2296 | [13 empty] | 0
2020-02-20 | 2380 | [13 empty] | 0
2020-02-21 | 1843 | [13 empty] | 0
2020-02-22 | 1831 | [13 empty] | 0
2020-02-23 | 1973 | [13 empty] | 6
2020-02-24 | 1768 | [13 empty] | 11
2020-02-25 | 1795 | [13 empty] | 10
2020-02-26 | 1845 | [13 empty] | 1
2020-02-27 | 1726 | [13 empty] | 6
2020-02-28 | 2035 | [13 empty] | 0
2020-02-29 | 1794 | [13 empty] | 5
2020-03-01 | 1315 | [13 empty] | 1
2020-03-02 | 1826 | 0.31 | 1 | 7.5 | 1 | 5 | 2 | 4.1 | 0.06 | 3.65 | 7.49 | 1.83 | 0.11 | 9.13 | 0 | 11:45 | 2020-03-11 | 2020-03-11
2020-03-03 | 1644 | [13 empty] | 0
2020-03-04 | 1549 | [13 empty] | 0
2020-03-05 | 1302 | [13 empty] | 0
2020-03-06 | 1570 | [13 empty] | 0
2020-03-07 | 1823 | [13 empty] | 37
2020-03-08 | 2124 | [13 empty] | 24
2020-03-09 | 2235 | [13 empty] | 1
2020-03-10 | 2107 | [13 empty] | 11
2020-03-11 | 2460 | [13 empty] | 0
2020-03-12 | 1613 | [13 empty] | 3
2020-03-13 | 1879 | [13 empty] | 5
2020-03-14 | 1931 | [13 empty] | 0
2020-03-15 | 1779 | [13 empty] | 9
2020-03-16 | 1817 | 0.46 | 1 | 7.3 | 1 | 3 | 1 | 5 | 0.12 | 1.82 | 9.09 | 1.82 | 0.22 | 5.45 | 14 | 10:30 | 2020-03-26 | 2020-03-26
2020-03-17 | 2100 | [13 empty] | 0
2020-03-18 | 1689 | [13 empty] | 0
2020-03-19 | 1699 | [13 empty] | 2
2020-03-20 | 1642 | [13 empty] | 0
2020-03-21 | 1318 | [13 empty] | 0
2020-03-22 | 1729 | [13 empty] | 0
2020-03-23 | 1519 | [13 empty] | 1
2020-03-24 | 1517 | [13 empty] | 3
2020-03-25 | 1472 | [13 empty] | 2
2020-03-26 | 1272 | [13 empty] | 0
2020-03-27 | 1589 | [13 empty] | 6
2020-03-28 | 1301 | [13 empty] | 3
2020-03-29 | 1489 | [13 empty] | 3
2020-03-30 | 1663 | 0.45 | 1 | 7.2 | 1 | 3 | 1 | 3.9 | 0.07 | 1.66 | 6.49 | 1.66 | 0.12 | 4.99 | 14 | 9:00 | 2020-04-08 | 2020-04-08
2020-03-31 | 1329 | [13 empty] | 3
2020-04-01 | 1424 | [13 empty] | 0
2020-04-02 | 1460 | [13 empty] | 0
2020-04-03 | 1278 | [13 empty] | 0
2020-04-04 | 1492 | [13 empty] | 0
2020-04-05 | 1257 | [13 empty] | 2
2020-04-06 | 1374 | [13 empty] | 0
2020-04-07 | 1383 | [13 empty] | 0
2020-04-08 | 1204 | [13 empty] | 22
2020-04-09 | 1527 | [13 empty] | 0
2020-04-10 | 1533 | [13 empty] | 21
2020-04-11 | 1547 | [13 empty] | 18
2020-04-12 | 1980 | [13 empty] | 0
2020-04-13 | 1361 | 0.43 | 1 | 7.3 | 1 | 4 | 1 | 4 | 0.14 | 1.36 | 5.44 | 1.36 | 0.19 | 5.44 | 14 | 8:45 | 2020-04-24 | 2020-04-24
2020-04-14 | 1201 | [13 empty] | 0
2020-04-15 | 1819 | [13 empty] | 0
2020-04-16 | 1155 | [13 empty] | 0
2020-04-17 | 1516 | [13 empty] | 0
2020-04-18 | 1379 | [13 empty] | 0
2020-04-19 | 1156 | [13 empty] | 0
2020-04-20 | 1318 | [13 empty] | 0
2020-04-21 | 1314 | [13 empty] | 0
2020-04-22 | 943 | [13 empty] | 0
2020-04-23 | 1215 | [13 empty] | 0
2020-04-24 | 1380 | [13 empty] | 0
2020-04-25 | 958 | [13 empty] | 0
2020-04-26 | 1455 | [13 empty] | 0
2020-04-27 | 1278 | 0.44 | 1 | 7.4 | 2 | 6 | 2 | 3.4 | 0.15 | 2.56 | 4.35 | 1.28 | 0.19 | 7.67 | 0 | 10:00 | 2020-05-11 | 2020-05-11
2020-04-28 | 1207 | [13 empty] | 7
2020-04-29 | 1239 | [13 empty] | 3
2020-04-30 | 1033 | [13 empty] | 0
2020-05-01 | 1321 | [13 empty] | 0
2020-05-02 | 1488 | [13 empty] | 0
2020-05-03 | 691 | [13 empty] | 0
2020-05-04 | 1509 | [13 empty] | 0
2020-05-05 | 1285 | [13 empty] | 0
2020-05-06 | 951 | [13 empty] | 5
2020-05-07 | 1649 | [13 empty] | 3
2020-05-08 | 1254 | [13 empty] | 0
2020-05-09 | 1105 | [13 empty] | 0
2020-05-10 | 976 | [13 empty] | 5
2020-05-11 | 1358 | 0.28 | 1 | 7.1 | 3 | 5 | 2 | 4.6 | 0.11 | 2.72 | 6.25 | 1.36 | 0.15 | 6.79 | 0 | 8:15 | 2020-05-19 | 2020-05-20
2020-05-12 | 1389 | [13 empty] | 0
2020-05-13 | 583 | [13 empty] | 0
2020-05-14 | 1195 | [13 empty] | 0
2020-05-15 | 1693 | [13 empty] | 0
2020-05-16 | 1266 | [13 empty] | 8
2020-05-17 | 675 | [13 empty] | 17
2020-05-18 | 1945 | [13 empty] | 27
2020-05-19 | 1606 | [13 empty] | 1
2020-05-20 | 1388 | [13 empty] | 4
2020-05-21 | 1403 | [13 empty] | 0
2020-05-22 | 1474 | [13 empty] | 3
2020-05-23 | 1414 | [13 empty] | 0
2020-05-24 | 1119 | [13 empty] | 0
2020-05-25 | 1318 | 0.31 | 1 | 7.3 | 1 | 6 | 2 | 3.7 | 0.1 | 2.64 | 4.88 | 1.32 | 0.13 | 7.91 | 0 | 8:15 | 2020-06-09 | 2020-06-09
2020-05-26 | 1481 | [13 empty] | 0
2020-05-27 | 1278 | [13 empty] | 0
2020-05-28 | 1062 | [13 empty] | 0
2020-05-29 | 1159 | [13 empty] | 0
2020-05-30 | 1448 | [13 empty] | 6
2020-05-31 | 1225 | [13 empty] | 8
MINIMUM | 81 | 0.28 | 1 | 7 | 1 | 3 | 1 | 2.91 | 0.06 | 0.93 | 3.59 | 0.74 | 0.11 | 2.23 | 0
AVERAGE | 1368.4126 | 0.65296 | 1.0769 | 7.3019 | 2.0833 | 5.963 | 2.037 | 4.6263 | 0.22 | 2.6659 | 6.2681 | 1.4637 | 0.29815 | 8.3707 | 3.4768
MAXIMUM | 5572 | 1.6 | 2 | 7.6 | 6 | 36 | 7 | 6.7 | 1.4 | 10.16 | 16.65 | 3.14 | 2.03 | 52.27 | 178
| Sample Count | 27 | [6 empty] | Total | 71.98 | 169.24 | 39.52 | 8.05 | 226.01 | 1276

## 20-21
Fortnightly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 20/21
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - | - | - | -
2020-06-01 | 1390 | [13 empty] | 0
2020-06-02 | 1190 | [13 empty] | 1
2020-06-03 | 1462 | [13 empty] | 0
2020-06-04 | 955 | [13 empty] | 0
2020-06-05 | 1416 | [13 empty] | 0
2020-06-06 | 1020 | [13 empty] | 0
2020-06-07 | 1354 | [13 empty] | 0
2020-06-08 | 1248 | 0.38 | 1 | 7.2 | 1 | 5 | 1 | 4.3 | 0.13 | 1.25 | 5.37 | 1.25 | 0.16 | 6.24 | 0 | 9:15 | 2020-06-23 | 2020-06-23
2020-06-09 | 1337 | [13 empty] | 0
2020-06-10 | 1131 | [13 empty] | 5
2020-06-11 | 1955 | [13 empty] | 31
2020-06-12 | 1567 | [13 empty] | 0
2020-06-13 | 1612 | [13 empty] | 0
2020-06-14 | 1581 | [13 empty] | 0
2020-06-15 | 1747 | [13 empty] | 20
2020-06-16 | 1685 | [13 empty] | 0
2020-06-17 | 1534 | [13 empty] | 0
2020-06-18 | 1397 | [13 empty] | 2
2020-06-19 | 1565 | [13 empty] | 10
2020-06-20 | 1368 | [13 empty] | 3
2020-06-21 | 1634 | [13 empty] | 1
2020-06-22 | 1805 | 0.3 | 1 | 7.1 | 32 | 9 | 2 | 4.2 | 0.1 | 3.61 | 7.58 | 1.81 | 0.18 | 16.25 | 0 | 7:30 | 2020-06-29 | 2020-06-29
2020-06-23 | 1539 | [13 empty] | 0
2020-06-24 | 1224 | [13 empty] | 0
2020-06-25 | 1639 | [13 empty] | 0
2020-06-26 | 1385 | [13 empty] | 0
2020-06-27 | 1234 | [13 empty] | 0
2020-06-28 | 1579 | [13 empty] | 10
2020-06-29 | 1361 | [13 empty] | 0
2020-06-30 | 1401 | [13 empty] | 3
2020-07-01 | 1558 | [13 empty] | 0
2020-07-02 | 1260 | [13 empty] | 0
2020-07-03 | 1269 | [13 empty] | 0
2020-07-04 | 1532 | [13 empty] | 2
2020-07-05 | 1417 | [13 empty] | 0
2020-07-06 | 1303 | 0.77 | 1 | 7.4 | 3 | 4 | 4 | 4.8 | 0.21 | 5.21 | 6.25 | 1.3 | 0.27 | 5.21 | 0 | 7:30 | 2020-07-16 | 2020-07-16
2020-07-07 | 1651 | [13 empty] | 0
2020-07-08 | 1299 | [13 empty] | 0
2020-07-09 | 1615 | [13 empty] | 26
2020-07-10 | 1000 | [13 empty] | 1
2020-07-11 | 1843 | [13 empty] | 0
2020-07-12 | 1610 | [13 empty] | 1
2020-07-13 | 1395 | [13 empty] | 2
2020-07-14 | 1058 | [13 empty] | 0
2020-07-15 | 1796 | [13 empty] | 0
2020-07-16 | 1233 | [13 empty] | 0
2020-07-17 | 1408 | [13 empty] | 0
2020-07-18 | 1335 | [13 empty] | 0
2020-07-19 | 1323 | [13 empty] | 0
2020-07-20 | 1625 | 0.42 | 1 | 7.3 | 2 | 6 | 2 | 4.2 | 0.12 | 3.25 | 6.83 | 1.63 | 0.2 | 9.75 | 0 | 9:30 | 2020-07-28 | 2020-07-28
2020-07-21 | 934 | [13 empty] | 0
2020-07-22 | 1660 | [13 empty] | 1
2020-07-23 | 724 | [13 empty] | 1
2020-07-24 | 1646 | [13 empty] | 42
2020-07-25 | 2589 | [13 empty] | 25
2020-07-26 | 2762 | [13 empty] | 36
2020-07-27 | 3913 | [13 empty] | 49
2020-07-28 | 2763 | [13 empty] | 0
2020-07-29 | 2227 | [13 empty] | 0
2020-07-30 | 1878 | [13 empty] | 0
2020-07-31 | 2006 | [13 empty] | 0
2020-08-01 | 1776 | [13 empty] | 2
2020-08-02 | 1734 | [13 empty] | 0
2020-08-03 | 1692 | 0.55 | 1 | 7.3 | 3 | 5 | 2 | 4.4 | 0.12 | 3.38 | 7.44 | 1.69 | 0.2 | 8.46 | 0 | 10:00 | 2020-08-17 | 2020-08-17
2020-08-04 | 1743 | [13 empty] | 0
2020-08-05 | 1841 | [13 empty] | 0
2020-08-06 | 1504 | [13 empty] | 0
2020-08-07 | 1344 | [13 empty] | 0
2020-08-08 | 2000 | [13 empty] | 18
2020-08-09 | 1475 | [13 empty] | 0
2020-08-10 | 1543 | [13 empty] | 0
2020-08-11 | 1496 | [13 empty] | 0
2020-08-12 | 1256 | [13 empty] | 0
2020-08-13 | 1563 | [13 empty] | 0
2020-08-14 | 1323 | [13 empty] | 0
2020-08-15 | 1663 | [13 empty] | 12
2020-08-16 | 1817 | [13 empty] | 2
2020-08-17 | 1533 | 0.45 | 1 | 7.3 | 2 | 4 | 1 | 3.9 | 0.09 | 1.53 | 5.98 | 1.53 | 0.14 | 6.13 | 0 | 8:00 | 2020-08-24 | 2020-08-24
2020-08-18 | 1286 | [13 empty] | 0
2020-08-19 | 1502 | [13 empty] | 0
2020-08-20 | 1313 | [13 empty] | 0
2020-08-21 | 1423 | [13 empty] | 0
2020-08-22 | 1379 | [13 empty] | 0
2020-08-23 | 1701 | [13 empty] | 0
2020-08-24 | 1213 | [13 empty] | 0
2020-08-25 | 1386 | [13 empty] | 0
2020-08-26 | 1372 | [13 empty] | 3
2020-08-27 | 1523 | [13 empty] | 0
2020-08-28 | 1203 | [13 empty] | 0
2020-08-29 | 1407 | [13 empty] | 0
2020-08-30 | 1775 | [13 empty] | 0
2020-08-31 | 1070 | 0.99 | 1 | 7.3 | 14 | 5 | 2 | 4.1 | 0.14 | 2.14 | 4.39 | 1.07 | 0.15 | 5.35 | 0 | 10:30 | 2020-09-14 | 2020-09-21
2020-09-01 | 1773 | [13 empty] | 0
2020-09-02 | 1079 | [13 empty] | 4
2020-09-03 | 1394 | [13 empty] | 0
2020-09-04 | 1161 | [13 empty] | 0
2020-09-05 | 1614 | [13 empty] | 0
2020-09-06 | 853 | [13 empty] | 2
2020-09-07 | 1652 | [13 empty] | 0
2020-09-08 | 1246 | [13 empty] | 0
2020-09-09 | 1100 | [13 empty] | 0
2020-09-10 | 1183 | [13 empty] | 13
2020-09-11 | 1425 | [13 empty] | 17
2020-09-12 | 1736 | [13 empty] | 3
2020-09-13 | 1215 | [13 empty] | 1
2020-09-14 | 1346 | 0.71 | 1 | 7.2 | 1 | 6 | 1 | 3.8 | 0.11 | 1.35 | 5.11 | 1.35 | 0.15 | 8.08 | 0 | 13:30 | 2020-09-29 | 2020-09-29
2020-09-15 | 1466 | [13 empty] | 0
2020-09-16 | 1243 | [13 empty] | 0
2020-09-17 | 1243 | [13 empty] | 0
2020-09-18 | 1267 | [13 empty] | 0
2020-09-19 | 1164 | [13 empty] | 0
2020-09-20 | 1227 | [13 empty] | 3
2020-09-21 | 1392 | [13 empty] | 0
2020-09-22 | 1269 | [13 empty] | 0
2020-09-23 | 1244 | [13 empty] | 2
2020-09-24 | 1210 | [13 empty] | 0
2020-09-25 | 1133 | [13 empty] | 0
2020-09-26 | 999 | [13 empty] | 0
2020-09-27 | 1567 | [13 empty] | 0
2020-09-28 | 1336 | 0.67 | 1 | 7.2 | 1 | 2 | 2 | 5.2 | 0.12 | 2.67 | 6.95 | 1.34 | 0.16 | 2.67 | 0 | 10:00 | 2020-10-09 | 2020-10-09
2020-09-29 | 1213 | [13 empty] | 3
2020-09-30 | 1218 | [13 empty] | 0
2020-10-01 | 769 | [13 empty] | 0
2020-10-02 | 1492 | [13 empty] | 0
2020-10-03 | 1363 | [13 empty] | 0
2020-10-04 | 1464 | [13 empty] | 0
2020-10-05 | 1464 | [13 empty] | 0
2020-10-06 | 1494 | [13 empty] | 0
2020-10-07 | 1177 | [13 empty] | 0
2020-10-08 | 1416 | [13 empty] | 0
2020-10-09 | 779 | [13 empty] | 0
2020-10-10 | 1526 | [13 empty] | 0
2020-10-11 | 1175 | [13 empty] | 0
2020-10-12 | 1276 | 0.83 | 1 | 7.3 | 6 | 4 | 2 | 4.8 | 0.17 | 2.55 | 6.12 | 1.28 | 0.22 | 5.1 | 0 | 10:00 | 2020-10-22 | 2020-10-22
2020-10-13 | 1175 | [13 empty] | 0
2020-10-14 | 1147 | [13 empty] | 0
2020-10-15 | 1100 | [13 empty] | 0
2020-10-16 | 1095 | [13 empty] | 0
2020-10-17 | 511 | [13 empty] | 0
2020-10-18 | 1294 | [13 empty] | 0
2020-10-19 | 1303 | [13 empty] | 10
2020-10-20 | 1400 | [13 empty] | 2
2020-10-21 | 1235 | [13 empty] | 0
2020-10-22 | 1222 | [13 empty] | 0
2020-10-23 | 1114 | [13 empty] | 0
2020-10-24 | 1082 | [13 empty] | 0
2020-10-25 | 881 | [13 empty] | 3
2020-10-26 | 1118 | 0.54 | 1 | 7.2 | 2 | 6 | 1 | 3.4 | 0.14 | 1.12 | 3.8 | 1.12 | 0.16 | 6.71 | 0 | 10:00 | 2020-11-04 | 2020-11-04
2020-10-27 | 1311 | [13 empty] | 0
2020-10-28 | 1284 | [13 empty] | 7
2020-10-29 | 1069 | [13 empty] | 4
2020-10-30 | 753 | [13 empty] | 4
2020-10-31 | 1799 | [13 empty] | 0
2020-11-01 | 1212 | [13 empty] | 0
2020-11-02 | 878 | [13 empty] | 0
2020-11-03 | 1486 | [13 empty] | 0
2020-11-04 | 1128 | [13 empty] | 0
2020-11-05 | 969 | [13 empty] | 0
2020-11-06 | 1178 | [13 empty] | 0
2020-11-07 | 1196 | [13 empty] | 6
2020-11-08 | 1138 | [13 empty] | 8
2020-11-09 | 1189 | 0.73 | 1 | 7.6 | 11 | 2 | 1 | 5 | 0.21 | 1.19 | 5.95 | 1.19 | 0.25 | 2.38 | 0 | 9:15 | 2020-11-19 | 2020-11-19
2020-11-10 | 1203 | [13 empty] | 3
2020-11-11 | 1218 | [13 empty] | 0
2020-11-12 | 693 | [13 empty] | 0
2020-11-13 | 1409 | [13 empty] | 0
2020-11-14 | 575 | [13 empty] | 1
2020-11-15 | 1566 | [13 empty] | 0
2020-11-16 | 1297 | [13 empty] | 0
2020-11-17 | 1122 | [13 empty] | 2
2020-11-18 | 1110 | [13 empty] | 0
2020-11-19 | 1058 | [13 empty] | 0
2020-11-20 | 498 | [13 empty] | 0
2020-11-21 | 1214 | [13 empty] | 0
2020-11-22 | 1176 | [13 empty] | 0
2020-11-23 | 1435 | 0.56 | 1 | 7.4 | 1 | 11 | 1 | 3.5 | 0.18 | 1.44 | 5.02 | 1.44 | 0.26 | 15.79 | 0 | 9:45 | 2020-12-03 | 2020-12-03
2020-11-24 | 1181 | [13 empty] | 0
2020-11-25 | 419 | [13 empty] | 0
2020-11-26 | 1271 | [13 empty] | 0
2020-11-27 | 1286 | [13 empty] | 0
2020-11-28 | 988 | [13 empty] | 0
2020-11-29 | 1303 | [13 empty] | 0
2020-11-30 | 825 | [13 empty] | 0
2020-12-01 | 1379 | [13 empty] | 0
2020-12-02 | 1019 | [13 empty] | 0
2020-12-03 | 1004 | [13 empty] | 2
2020-12-04 | 1093 | [13 empty] | 0
2020-12-05 | 1054 | [13 empty] | 0
2020-12-06 | 1104 | [13 empty] | 0
2020-12-07 | 1150 | 0.44 | 1 | 7.5 | 5 | 3 | 2 | 3.7 | 0.26 | 2.3 | 4.26 | 1.15 | 0.3 | 3.45 | 0 | 11:30 | 2020-12-22 | 2020-12-22
2020-12-08 | 991 | [13 empty] | 2
2020-12-09 | 1353 | [13 empty] | 0
2020-12-10 | 995 | [13 empty] | 0
2020-12-11 | 1199 | [13 empty] | 0
2020-12-12 | 1070 | [13 empty] | 63
2020-12-13 | 1305 | [13 empty] | 30
2020-12-14 | 2264 | [13 empty] | 10
2020-12-15 | 1876 | [13 empty] | 66
2020-12-16 | 2936 | [13 empty] | 8
2020-12-17 | 3959 | [13 empty] | 3
2020-12-18 | 2865 | [13 empty] | 8
2020-12-19 | 2493 | [13 empty] | 1
2020-12-20 | 2193 | [13 empty] | 0
2020-12-21 | 1814 | 2.3 | <2 | 7.4 | 10 | <1 | Not Tested | 5.2 | 0.33 | Not tested | 9.43 | 1.81 | 0.6 | 0.6 | 74 | 12:10 | 2021-01-06 | 2021-01-07
2020-12-22 | 2394 | [13 empty] | 1
2020-12-23 | 3015 | [13 empty] | 0
2020-12-24 | 2259 | [13 empty] | 0
2020-12-25
2020-12-26 | 2318 | [13 empty] | 0
2020-12-27 | 1669 | [13 empty] | 0
2020-12-28 | 2151 | [13 empty] | 0
2020-12-29 | 2050 | [13 empty] | 0
2020-12-30 | 1988 | [13 empty] | 122
2020-12-31 | 2151 | [13 empty] | 0
2021-01-01 | 5279 | [13 empty] | 1
2021-01-02 | 3050 | [13 empty] | 9
2021-01-03 | 2702 | [13 empty] | 3
2021-01-04 | 2774 | 0.9 | <2 | 7 | <1 | 4 | <2 | 2.8 | 0.15 | 2.77 | 7.77 | 2.77 | 0.42 | 11.1 | 0 | 9:30 | 2021-01-11 | 2021-01-14
2021-01-05 | 2591 | [13 empty] | 6
2021-01-06 | 2074 | [13 empty] | 2
2021-01-07 | 2611 | [13 empty] | 10
2021-01-08 | 1994 | [13 empty] | 34
2021-01-09 | 2885 | [13 empty] | 22
2021-01-10 | 2887 | [13 empty] | 2
2021-01-11 | 2965 | [13 empty] | 1
2021-01-12 | 2590 | [13 empty] | 0
2021-01-13 | 2296 | [13 empty] | 0
2021-01-14 | 2404 | [13 empty] | 0
2021-01-15 | 2080 | [13 empty] | 0
2021-01-16 | 1957 | [13 empty] | 2
2021-01-17 | 2204 | [13 empty] | 0
2021-01-18 | 1618 | 0.74 | 1 | 7.3 | 1 | 7 | 3 | 3.8 | 0.13 | 4.85 | 6.15 | 4.62 | 0.21 | 11.33 | 0 | 12:30 | 2021-01-27 | 2021-01-28
2021-01-19 | 1935 | [13 empty] | 14
2021-01-20 | 2035 | [13 empty] | 9
2021-01-21 | 1500 | [13 empty] | 6
2021-01-22 | 1673 | [13 empty] | 0
2021-01-23 | 1685 | [13 empty] | 0
2021-01-24 | 1456 | [13 empty] | 0
2021-01-25 | 2073 | [13 empty] | 0
2021-01-26 | 1456 | [13 empty] | 0
2021-01-27 | 1715 | [13 empty] | 0
2021-01-28 | 1642 | [13 empty] | 0
2021-01-29 | 1546 | [13 empty] | 0
2021-01-30 | 1173 | [13 empty] | 0
2021-01-31 | 1614 | [13 empty] | 3
2021-02-01 | 1576 | 0.61 | 1 | 7.2 | 1 | 6 | 2 | 5 | 0.16 | 3.15 | 7.88 | 1.58 | 0.25 | 9.46 | 1 | 8:45 | 2021-02-08 | 2021-02-12
2021-02-02 | 1223 | [13 empty] | 2
2021-02-03 | 1293 | [13 empty] | 25
2021-02-04 | 1436 | [13 empty] | 2
2021-02-05 | 1939 | [13 empty] | 0
2021-02-06 | 1366 | [13 empty] | 0
2021-02-07 | 1289 | [13 empty] | 0
2021-02-08 | 1213 | [13 empty] | 0
2021-02-09 | 1516 | [13 empty] | 1
2021-02-10 | 1225 | [13 empty] | 0
2021-02-11 | 1400 | [13 empty] | 2
2021-02-12 | 1115 | [13 empty] | 0
2021-02-13 | 1407 | [13 empty] | 0
2021-02-14 | 1388 | [13 empty] | 13
2021-02-15 | 1484 | 0.59 | 1 | 7.1 | 1 | 5 | 2 | 4.3 | 0.14 | 2.97 | 6.38 | 2.97 | 0.21 | 7.42 | 7 | 9:00 | 2021-02-25 | 2021-03-01
2021-02-16 | 1216 | [13 empty] | 1
2021-02-17 | 1240 | [13 empty] | 16
2021-02-18 | 1677 | [13 empty] | 26
2021-02-19 | 1761 | [13 empty] | 7
2021-02-20 | 1953 | [13 empty] | 69
2021-02-21 | 2469 | [13 empty] | 19
2021-02-22 | 3682 | [13 empty] | 10
2021-02-23 | 2226 | [13 empty] | 0
2021-02-24 | 2647 | [13 empty] | 38
2021-02-25 | 2086 | [13 empty] | 11
2021-02-26 | 3328 | [13 empty] | 1
2021-02-27 | 2756 | [13 empty] | 0
2021-02-28 | 2285 | [13 empty] | 0
2021-03-01 | 2060 | 0.5 | 1 | 7 | 3 | 7 | 1 | 3.7 | 0.16 | 2.06 | 7.62 | 2.06 | 0.33 | 14.42 | 0 | 09:00:00AM | 11.03.2021 | 11.03.2021
2021-03-02 | 2046 | [13 empty] | 1
2021-03-03 | 1986 | [13 empty] | 1
2021-03-04 | 1994 | [13 empty] | 24
2021-03-05 | 1893 | [13 empty] | 1
2021-03-06 | 2284 | [13 empty] | 3
2021-03-07 | 1643 | [13 empty] | 5
2021-03-08 | 1646 | [13 empty] | 0
2021-03-09 | 1876 | [13 empty] | 16
2021-03-10 | 1522 | [13 empty] | 2
2021-03-11 | 1671 | [13 empty] | 31
2021-03-12 | 2455 | [13 empty] | 16
2021-03-13 | 3872 | [13 empty] | 0
2021-03-14 | 2824 | [13 empty] | 0
2021-03-15 | 2254 | 0.35 | 1 | 7.4 | 1 | 9 | 2 | 4.3 | 0.2 | 4.51 | 9.69 | 2.25 | 0.45 | 20.29 | 21 | 12:00:00PM | 29.03.2021 | 29.03.2021
2021-03-16 | 2209 | [13 empty] | 10
2021-03-17 | 2864 | [13 empty] | 3
2021-03-18 | 2074 | [13 empty] | 8
2021-03-19 | 2254 | [13 empty] | 12
2021-03-20 | 2760 | [13 empty] | 23
2021-03-21 | 2301 | [13 empty] | 25
2021-03-22 | 2285 | [13 empty] | 101
2021-03-23 | 7573 | [13 empty] | 59
2021-03-24 | 9181 | [13 empty] | 36
2021-03-25 | 6665 | [13 empty] | 0
2021-03-26 | 4885 | [13 empty] | 0
2021-03-27 | 3450 | [13 empty] | 0
2021-03-28 | 2551 | [13 empty] | 0
2021-03-29 | 2730 | 0.3 | 1 | 7.1 | 1 | 9 | 3 | 2.8 | 0.24 | 8.19 | 7.64 | 2.73 | 0.66 | 24.57 | 0 | 09:30:00AM | 13.04.2021 | 13.04.2021
2021-03-30 | 2702 | [13 empty] | 6
2021-03-31 | 2573 | [13 empty] | 2
2021-04-01 | 2960 | [13 empty] | 7
2021-04-02 | 3126 | [13 empty] | 36
2021-04-03 | 3111 | [13 empty] | 2
2021-04-04 | 2697 | [13 empty] | 1
2021-04-05 | 2530 | [13 empty] | 13
2021-04-06 | 3147 | [13 empty] | 23
2021-04-07 | 4255 | [13 empty] | 30
2021-04-08 | 4551 | [13 empty] | 13
2021-04-09 | 4620 | [13 empty] | 11
2021-04-10 | 3660 | [13 empty] | 0
2021-04-11 | 2934 | [13 empty] | 0
2021-04-12 | 2619 | 0.5 | 1 | 7 | 1 | 10 | 2 | 4.2 | 0.22 | 5.24 | 11 | 2.62 | 0.58 | 26.19 | 0 | 08:10:00AM | 05.05.2021 | 05.05.2021
2021-04-13 | 2619 | [13 empty] | 0
2021-04-14 | 1578 | [13 empty] | 0
2021-04-15 | 2260 | [13 empty] | 0
2021-04-16 | 2277 | [13 empty] | 0
2021-04-17 | 2204 | [13 empty] | 0
2021-04-18 | 2117 | [13 empty] | 6
2021-04-19 | 2166 | [13 empty] | 0
2021-04-20 | 1908 | [13 empty] | 0
2021-04-21 | 1615 | [13 empty] | 0
2021-04-22 | 2045 | [13 empty] | 0
2021-04-23 | 2045 | [13 empty] | 0
2021-04-24 | 1811 | [13 empty] | 0
2021-04-25 | 1797 | [13 empty] | 0
2021-04-26 | 1794 | [13 empty] | 0
2021-04-27 | 1794 | [13 empty] | 5
2021-04-28 | 1629 | 0.59 | 1 | 7.1 | 2 | 7 | 2 | 3.8 | 0.16 | 3.59 | 6.82 | 1.79 | 0.29 | 12.56 | 5 | 07:50:00AM | 10.05.2021 | 10.05.2021
2021-04-29 | 1858 | [13 empty] | 24
2021-04-30 | 1892 | [13 empty] | 3
2021-05-01 | 1892 | [13 empty] | 35
2021-05-02 | 2356 | [13 empty] | 0
2021-05-03 | 2580 | [13 empty] | 0
2021-05-04 | 1899 | [13 empty] | 0
2021-05-05 | 1821 | [13 empty] | 1
2021-05-06 | 2188 | [13 empty] | 15
2021-05-07 | 2038 | [13 empty] | 0
2021-05-08 | 1423 | [13 empty] | 0
2021-05-09 | 2198 | [13 empty] | 0
2021-05-10 | 1436 | [13 empty] | 0
2021-05-11 | 1707 | [13 empty] | 0
2021-05-12 | 1365 | [13 empty] | 1
2021-05-13 | 2216 | 0.59 | 1 | 7.1 | 2 | 7 | 2 | 0.17 | 0.16 | 3.41 | 6.49 | 1.71 | 0.27 | 11.95 | 3 | 07:50:00AM | 10.05.2021 | 10.05.2021
2021-05-14 | 1264 | [13 empty] | 0
2021-05-15 | 1610 | [13 empty] | 0
2021-05-16 | 1732 | [13 empty] | 0
2021-05-17 | 1618 | [13 empty] | 0
2021-05-18 | 1543 | [13 empty] | 3
2021-05-19 | 1750 | [13 empty] | 3
2021-05-20 | 1509 | [13 empty] | 2
2021-05-21 | 1628 | [13 empty] | 0
2021-05-22 | 1514 | [13 empty] | 4
2021-05-23 | 1348 | [13 empty] | 10
2021-05-24 | 1320 | [13 empty] | 18
2021-05-25 | 1715 | [13 empty] | 1
2021-05-26 | 1244 | 0.51 | 1 | 7.1 | 4 | 5 | 2 | 3.1 | 0.09 | 2.64 | 4.09 | 1.32 | 0.12 | 6.6 | 0 | 10:00:00AM | 26.05.2021 | 26.05.2021
2021-05-27 | 2000 | [13 empty] | 0
2021-05-28 | 1515 | [13 empty] | 0
2021-05-29 | 1483 | [13 empty] | 0
2021-05-30 | 1676 | [13 empty] | 0
2021-05-31 | 1121 | [13 empty] | 0
MINIMUM | 419 | 0.3 | 1 | 7 | 1 | 2 | 1 | 0.17 | 0.09 | 1.12 | 3.8 | 1.07 | 0.12 | 0.6 | 0
AVERAGE | 1770.5 | 0.64692 | 1 | 7.2346 | 4.44 | 5.92 | 1.875 | 3.9412 | 0.16308 | 3.0548 | 6.6158 | 1.8223 | 0.27654 | 9.9254 | 5.0907
MAXIMUM | 9181 | 2.3 | 1 | 7.6 | 32 | 11 | 4 | 5.2 | 0.33 | 8.19 | 11 | 4.62 | 0.66 | 26.19 | 122
| Sample Count | 26 | [6 empty] | Total | 76.37 | 172.01 | 47.38 | 7.19 | 258.06 | 1853

## 21-22
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 21/22
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Sampled By | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - |  | - | - | -
2021-06-01 | 1616 | [13 empty] | 0
2021-06-02 | 1639 | [13 empty] | 0
2021-06-03 | 1573 | [13 empty] | 0
2021-06-04 | 1513 | [13 empty] | 2
2021-06-05 | 1620 | [13 empty] | 0
2021-06-06 | 1579 | [13 empty] | 0
2021-06-07 | 1504 | [13 empty] | 0
2021-06-08 | 1588 | [13 empty] | 0
2021-06-09 | 1493 | 0.63 | 0.01 | 7.2 | 8 | 6 | 2 | 4.8 | 0.1 | 1.95 | 4.67 | 0.97 | 0.1 | 5.84 | 4 | Adrian O'Rourke | 10:30 | 24.06.2021 | 21.07.2021
2021-06-10 | 1662 | [13 empty] | 0
2021-06-11 | 1505 | [13 empty] | 0
2021-06-12 | 1467 | [13 empty] | 0
2021-06-13 | 1529 | [13 empty] | 0
2021-06-14 | 1396 | [13 empty] | 0
2021-06-15 | 1537 | [13 empty] | 1
2021-06-16 | 1288 | [13 empty] | 0
2021-06-17 | 1414 | [13 empty] | 4
2021-06-18 | 1481 | [13 empty] | 0
2021-06-19 | 1405 | [13 empty] | 0
2021-06-20 | 1418 | [13 empty] | 0
2021-06-21 | 1461 | [13 empty] | 0
2021-06-22 | 1328 | 1 | 0.05 | 7.3 | 1 | 1 | 2 | 3.2 | 0.11 | 1.58 | 5.04 | 1.58 | 0.17 | 1.58 | 1 | Adrian O'Rourke | 11:00 | 30.06.2021 | 21.07.2021
2021-06-23 | 1294 | [13 empty] | 9
2021-06-24 | 1358 | [13 empty] | 0
2021-06-25 | 1238 | [13 empty] | 1
2021-06-26 | 1405 | [13 empty] | 1
2021-06-27 | 1365 | [13 empty] | 0
2021-06-28 | 1486 | [13 empty] | 0
2021-06-29 | 1417 | [13 empty] | 15
2021-06-30 | 1476 | [13 empty] | 16
2021-07-01 | 1597 | [13 empty] | 16
2021-07-02 | 1717 | [13 empty] | 13
2021-07-03 | 1882 | [13 empty] | 5
2021-07-04 | 1588 | [13 empty] | 2
2021-07-05 | 1697 | [13 empty] | 0
2021-07-06 | 1625 | [13 empty] | 0
2021-07-07 | 1576 | 0.75 | 0.01 | 7.3 | 3 | 4 | 2 | 2.6 | 0.08 | 2.78 | 3.62 | 1.39 | 0.11 | 5.57 | 0 | Adrian O'Rourke | 10:48 | 16.07.2021 | 21.07.2021
2021-07-08 | 1642 | [13 empty] | 0
2021-07-09 | 1426 | [13 empty] | 6
2021-07-10 | 1514 | [13 empty] | 7
2021-07-11 | 1566 | [13 empty] | 0
2021-07-12 | 1472 | [13 empty] | 1
2021-07-13 | 1410 | [13 empty] | 0
2021-07-14 | 1489 | [13 empty] | 0
2021-07-15 | 1457 | [13 empty] | 0
2021-07-16 | 1423 | [13 empty] | 2
2021-07-17 | 1390 | [13 empty] | 3
2021-07-18 | 1423 | [13 empty] | 0
2021-07-19 | 1541 | [13 empty] | 0
2021-07-20 | 1480 | [13 empty] | 0
2021-07-21 | 1499 | 0.91 | 0.01 | 7.3 | <1 | 4 | 3 | 3.2 | 0.09 | 4.08 | 4.36 | 1.33 | 0.12 | 5.44 | 0 | Marc Schneider | 10:00 | 29.07.2021 | 13.08.2021
2021-07-22 | 1448 | [13 empty] | 0
2021-07-23 | 1519 | [13 empty] | 0
2021-07-24 | 1375 | [13 empty] | 1
2021-07-25 | 1403 | [13 empty] | 0
2021-07-26 | 1416 | [13 empty] | 0
2021-07-27 | 1456 | [13 empty] | 0
2021-07-28 | 1431 | [13 empty] | 0
2021-07-29 | 1412 | [13 empty] | 0
2021-07-30 | 1292 | [13 empty] | 0
2021-07-31 | 1417 | [13 empty] | 0
2021-08-01 | 1389 | [13 empty] | 0
2021-08-02 | 1439 | [13 empty] | 0
2021-08-03 | 1243 | 0.69 | 0.05 | 7.3 | 1 | 5 | 2 | 3.4 | 0.09 | 2.4 | 4.07 | 1.2 | 0.11 | 5.99 | 4 | Adrian O'Rourke | 10:15 | 10.08.2021 | 13.08.2021
2021-08-04 | 1319 | [13 empty] | 1
2021-08-05 | 1557 | [13 empty] | 0
2021-08-06 | 1386 | [13 empty] | 0
2021-08-07 | 1375 | [13 empty] | 0
2021-08-08 | 1399 | [13 empty] | 0
2021-08-09 | 1352 | [13 empty] | 4
2021-08-10 | 1255 | [13 empty] | 0
2021-08-11 | 1291 | [13 empty] | 0
2021-08-12 | 1424 | [13 empty] | 0
2021-08-13 | 1449 | [13 empty] | 2
2021-08-14 | 1234 | [13 empty] | 0
2021-08-15 | 1223 | [13 empty] | 0
2021-08-16 | 1252 | [13 empty] | 0
2021-08-17 | 1191 | [13 empty] | 0
2021-08-18 | 1372 | 0.5 | 0.01 | 7.4 | 96 | 6 | 2 | 4.2 | 0.11 | 2.54 | 5.33 | 0.94 | 0.14 | 7.61 | 1 | Adrian O'Rourke | 7:45 | 26.08.2021 | 08.09.2021
2021-08-19 | 1217 | [13 empty] | 0
2021-08-20 | 1171 | [13 empty] | 0
2021-08-21 | 1243 | [13 empty] | 0
2021-08-22 | 1173 | [13 empty] | 0
2021-08-23 | 1203 | [13 empty] | 0
2021-08-24 | 1137 | [13 empty] | 0
2021-08-25 | 1174 | [13 empty] | 7
2021-08-26 | 1210 | [13 empty] | 0
2021-08-27 | 1320 | [13 empty] | 0
2021-08-28 | 1252 | [13 empty] | 0
2021-08-29 | 1219 | [13 empty] | 0
2021-08-30 | 1183 | [13 empty] | 0
2021-08-31 | 1181 | [13 empty] | 0
2021-09-01 | 1120 | 0.45 | 0.01 | 7.3 | 4 | 6 | 2 | 4 | 0.14 | 2.254 | 4.508 | 1.127 | 0.15778 | 6.762 | 0 | Adrian O'Rourke | 11:00 | 09.09.2021 | 13.09.2021
2021-09-02 | 1112 | [13 empty] | 0
2021-09-03 | 1110 | [13 empty] | 1
2021-09-04 | 1162 | [13 empty] | 7
2021-09-05 | 1268 | [13 empty] | 1
2021-09-06 | 1097 | [13 empty] | 0
2021-09-07 | 1234 | [13 empty] | 2
2021-09-08 | 1118 | [13 empty] | 0
2021-09-09 | 1222 | [13 empty] | 0
2021-09-10 | 1150 | [13 empty] | 0
2021-09-11 | 1145 | [13 empty] | 0
2021-09-12 | 1161 | [13 empty] | 0
2021-09-13 | 1157 | [13 empty] | 0
2021-09-14 | 1126 | [13 empty] | 0
2021-09-15 | 1239 | 0.35 | 0.01 | 7.4 | 1 | 6 | 5 | 3.6 | 0.06 | 6.67 | 4.8 | 1.33 | 0.08 | 8 | 1 | Adrian O'Rourke | 8:30 | 07.10.2021 | 11.10.2021
2021-09-16 | 1181 | [13 empty] | 0
2021-09-17 | 1119 | [13 empty] | 0
2021-09-18 | 1161 | [13 empty] | 0
2021-09-19 | 1118 | [13 empty] | 0
2021-09-20 | 1145 | [13 empty] | 0
2021-09-21 | 1093 | [13 empty] | 6
2021-09-22 | 1155 | [13 empty] | 6
2021-09-23 | 1031 | [13 empty] | 0
2021-09-24 | 1105 | [13 empty] | 0
2021-09-25 | 1151 | [13 empty] | 0
2021-09-26 | 1079 | [13 empty] | 1.5
2021-09-27 | 1045 | [13 empty] | 0
2021-09-28 | 1287 | 0.49 | 0.05 | 7.2 | 1 | 5 | <2 | 3.8 | 0.12 | 1.29 | 4.89 | 1.29 | 0.15 | 6.44 | 0 | Marc Schneider | 9:40 | 08.10.2021 | 11.10.2021
2021-09-29 | 1115 | [13 empty] | 0
2021-09-30 | 823 | [13 empty] | 11
2021-10-01 | 1599 | [13 empty] | 6
2021-10-02 | 1168 | [13 empty] | 13
2021-10-03 | 1290 | [13 empty] | 0
2021-10-04 | 1290 | [13 empty] | 0
2021-10-05 | 948 | [13 empty] | 0
2021-10-06 | 1265 | [13 empty] | 0
2021-10-07 | 1234 | [13 empty] | 0
2021-10-08 | 1207 | [13 empty] | 0
2021-10-09 | 1091 | [13 empty] | 0
2021-10-10 | 1286 | [13 empty] | 0
2021-10-11 | 1141 | [13 empty] | 0
2021-10-12 | 1037 | [13 empty] | 0
2021-10-13 | 1750 | 0.49 | 0.01 | 7.4 | <1 | 8 | 3 | 4.2 | 0.21 | 3.11 | 4.36 | 2.07 | 0.22 | 8.3 | 25 | Adrian O'Rourke | 8:00 | 20.10.2021 | 20.10.2021
2021-10-14 | 1822 | [13 empty] | 54
2021-10-15 | 1509 | [13 empty] | 5
2021-10-16 | 1720 | [13 empty] | 0
2021-10-17 | 1277 | [13 empty] | 0
2021-10-18 | 1420 | [13 empty] | 0
2021-10-19 | 1217 | [13 empty] | 13
2021-10-20 | 1308 | [13 empty] | 2
2021-10-21 | 807 | [13 empty] | 0
2021-10-22 | 1782 | [13 empty] | 20
2021-10-23 | 1215 | [13 empty] | 0
2021-10-24 | 1248 | [13 empty] | 0
2021-10-25 | 1513 | [13 empty] | 0
2021-10-26 | 1298 | [13 empty] | 3
2021-10-27 | 1300 | 0.42 | 0.01 | 7.5 | <1 | 6 | 2 | 3.4 | 0.15 | 0.55 | 4.41 | 1.3 | 0.19 | 7.79 | 0 | Adrian O'Rourke | 8:30 | 02.11.2021 | 03.11.2021
2021-10-28 | 1361 | [13 empty] | 0
2021-10-29 | 1201 | [13 empty] | 0
2021-10-30 | 1238 | [13 empty] | 1
2021-10-31 | 1211 | [13 empty] | 1
2021-11-01 | 1246 | [13 empty] | 0
2021-11-02 | 1153 | [13 empty] | 2
2021-11-03 | 1218 | [13 empty] | 0
2021-11-04 | 1115 | [13 empty] | 0
2021-11-05 | 697 | [13 empty] | 0
2021-11-06 | 1615 | [13 empty] | 0
2021-11-07 | 1263 | [13 empty] | 2
2021-11-08 | 1310 | [13 empty] | 5
2021-11-09 | 747 | [13 empty] | 0
2021-11-10 | 1613 | [13 empty] | 22
2021-11-11 | 1246 | 0.66 | 0.01 | 7.2 | <1 | 4 | 2 | 3.6 | 0.19 | 3.23 | 5.81 | 1.61 | 0.31 | 6.45 | 2 | Adrian O'Rourke | 10:15 | 15.11.2021 | 16.11.2021
2021-11-12 | 1404 | [13 empty] | 1
2021-11-13 | 1061 | [13 empty] | 0
2021-11-14 | 1305 | [13 empty] | 0
2021-11-15 | 1568 | [13 empty] | 0
2021-11-16 | 1089 | [13 empty] | 0
2021-11-17 | 1180 | [13 empty] | 6
2021-11-18 | 1179 | [13 empty] | 0
2021-11-19 | 1281 | [13 empty] | 0
2021-11-20 | 1265 | [13 empty] | 0
2021-11-21 | 782 | [13 empty] | 27
2021-11-22 | 1649 | [13 empty] | 7
2021-11-23 | 1411 | 0.5 | 0.05 | 7.3 | <1 | 5 | <2 | 4.1 | 0.22 | 1.23 | 5.06 | 1.23 | 0.27 | 6.17 | 12 | Marc Schneider | 8:00 | 01.12.2021 | 01.12.2021
2021-11-24 | 1233 | [13 empty] | 2
2021-11-25 | 1394 | [13 empty] | 8
2021-11-26 | 1559 | [13 empty] | 4
2021-11-27 | 879 | [13 empty] | 12
2021-11-28 | 1711 | [13 empty] | 1
2021-11-29 | 1302 | [13 empty] | 0
2021-11-30 | 1377 | [13 empty] | 1
2021-12-01 | 2906 | [13 empty] | 107
2021-12-02 | 4057 | [13 empty] | 7
2021-12-03 | 2375 | [13 empty] | 2
2021-12-04 | 1841 | [13 empty] | 0
2021-12-05 | 2618 | [13 empty] | 22
2021-12-06 | 2315 | [13 empty] | 27
2021-12-07 | 3079 | [13 empty] | 19
2021-12-08 | 2421 | 0.61 | 0.01 | 7 | <1 | 2 | <2 | 3.7 | 0.23 | 6.16 | 11.39 | 6.16 | 0.71 | 6.16 | 2 | Adrian O'Rourke | 7:45 | 15.12.2021 | 16.12.2021
2021-12-09 | 2447 | [13 empty] | 23
2021-12-10 | 2864 | [13 empty] | 31
2021-12-11 | 2480 | [13 empty] | 0
2021-12-12 | 2435 | [13 empty] | 7
2021-12-13 | 1881 | [13 empty] | 1
2021-12-14 | 2079 | [13 empty] | 0
2021-12-15 | 1715 | 0.67 | 0.01 | 7.3 | <1 | 4 | <2 | 3.8 | 0.23 | 3.43 | 6.52 | 3.43 | 0.39 | 6.86 | 0 | Adrian O'Rourke | 7:45 | 04.01.2022 | 5.1.2022
2021-12-16 | 1694 | [13 empty] | 0
2021-12-17 | 1621 | [13 empty] | 0
2021-12-18 | 1454 | [13 empty] | 0
2021-12-19 | 1749 | [13 empty] | 0
2021-12-20 | 1549 | [13 empty] | 0
2021-12-21 | 1589 | [13 empty] | 0
2021-12-22 | 1505 | [13 empty] | 0
2021-12-23 | 1520 | [13 empty] | 0
2021-12-24 | 1476 | [13 empty] | 1
2021-12-25 | [14 empty] | 0
2021-12-26 | 1717 | [13 empty] | 2
2021-12-27 | 1575 | [13 empty] | 0
2021-12-28 | 1906 | [13 empty] | 36
2021-12-29 | 2218 | [13 empty] | 0
2021-12-30 | 2170 | [13 empty] | 8
2021-12-31 | 2167 | [13 empty] | 2
2022-01-01 | 2088 | [13 empty] | 2
2022-01-02 | 1981 | [13 empty] | 2
2022-01-03 | 1826 | [13 empty] | 9
2022-01-04 | 2125 | [13 empty] | 13
2022-01-05 | 1878 | 1.1 | 0.01 | 7.41 | 5 | 6 | 2 | 4.6 | 0.29 | 4.25 | 9.78 | 4.25 | 0.62 | 12.75 | 15 | Adrian O'Rourke | 9:45 | 12.01.2022 | 12.01.2022
2022-01-06 | 1967 | [13 empty] | 5
2022-01-07 | 2584 | [13 empty] | 14
2022-01-08 | 1948 | [13 empty] | 2
2022-01-09 | 1779 | [13 empty] | 0
2022-01-10 | 1715 | [13 empty] | 0
2022-01-11 | 1884 | [13 empty] | 3
2022-01-12 | 1785 | [13 empty] | 0
2022-01-13 | 1386 | [13 empty] | 0
2022-01-14 | 1416 | [13 empty] | 0
2022-01-15 | 1597 | [13 empty] | 0
2022-01-16 | 1861 | [13 empty] | 9
2022-01-17 | 1727 | [13 empty] | 9
2022-01-18 | 1293 | [13 empty] | 0
2022-01-19 | 1687 | 0.91 | 0.01 | 7.09 | <1 | 7 | 2 | 5.8 | 0.32 | 2.59 | 7.5 | 1.29 | 0.41 | 9.05 | 0 | Adrian O'Rourke | 10:00 | 25.01.2022 | 25.01.2022
2022-01-20 | 1683 | [13 empty] | 22
2022-01-21 | 2858 | [13 empty] | 34
2022-01-22 | 2382 | [13 empty] | 3
2022-01-23 | 2002 | [13 empty] | 11
2022-01-24 | 2123 | [13 empty] | 4
2022-01-25 | 1948 | [13 empty] | 1
2022-01-26 | 1595 | [13 empty] | 5
2022-01-27 | 1884 | [13 empty] | 0
2022-01-28 | 1483 | [13 empty] | 9
2022-01-29 | 1822 | [13 empty] | 3
2022-01-30 | 1742 | [13 empty] | 4
2022-01-31 | 1298 | [13 empty] | 3
2022-02-01 | 1554 | [13 empty] | 0
2022-02-02 | 1673 | 0.41 | <2 | 7.18 | 1 | 11 | <2 | 4.2 | 0.25 | 1.67 | 7.03 | 1.67 | 0.42 | 18.4 | 1 | Adrian O'Rourke | 9:45 | 11.02.2022 | 14.02.2022
2022-02-03 | 1960 | [13 empty] | 58
2022-02-04 | 4036 | [13 empty] | 50
2022-02-05 | 3122 | [13 empty] | 14
2022-02-06 | 2222 | [13 empty] | 2
2022-02-07 | 2352 | [13 empty] | 1
2022-02-08 | 1872 | [13 empty] | 9
2022-02-09 | 2015 | [13 empty] | 0
2022-02-10 | 1883 | [13 empty] | 0
2022-02-11 | 1667 | [13 empty] | 0
2022-02-12 | 1961 | [13 empty] | 3
2022-02-13 | 1682 | [13 empty] | 4
2022-02-14 | 1665 | [13 empty] | 6
2022-02-15 | 1412 | [13 empty] | 3
2022-02-16 | 1838 | 0.74 | <2 | 7.18 | 1 | 3 | <2 | 4.9 | 0.15 | 1.36 | 9.01 | 1.84 | 0.28 | 5.51 | 2 | Adrian O'Rourke | 0.40625 | 25.02.2022 | 28.02.2022
2022-02-17 | 1553 | [13 empty] | 0
2022-02-18 | 1717 | [13 empty] | 0
2022-02-19 | 1377 | [13 empty] | 1
2022-02-20 | 1818 | [13 empty] | 4
2022-02-21 | 1229 | [13 empty] | 1
2022-02-22 | 1727 | [13 empty] | 7
2022-02-23 | 1582 | [13 empty] | 2
2022-02-24 | 3009 | [13 empty] | 91
2022-02-25 | 4949 | [13 empty] | 18
2022-02-26 | 3012
2022-02-27
2022-02-28
2022-03-01 | 8343
2022-03-02
2022-03-03
2022-03-04 | 5248
2022-03-05 | 3854
2022-03-06 | 3575 | [13 empty] | 70
2022-03-07 | 3528 | [13 empty] | 40
2022-03-08 | 3974
2022-03-09 | 4260 | 2.2 | 2 | 6.7 | 13000 | 97 | 16 | 7.7 | 2.1 | 68.16 | 32.8 | 8.52 | 8.95 | 413.22 | 10 | Marc Schneider | 9:50 | 12.04.2022 | 13.04.2022
2022-03-10 | 3398
2022-03-11 | 3862 | [13 empty] | 9
2022-03-12 | 4198 | [13 empty] | 0
2022-03-13 | 3305
2022-03-14 | 2770 | [13 empty] | 10
2022-03-15 | 2681
2022-03-16 | 2505 | 0.43 | 1 | 7 | 290 | 12 | 2 | 1.9 | 0.04 | 5.01 | 4.76 | 2.51 | 0.09 | 30.06 |  | Adrian O'Rouke | 9.30 AM | 2022-05-06 | 2022-05-10
2022-03-17 | 2368 | [13 empty] | 7
2022-03-18 | 2211 | [13 empty] | 3
2022-03-19 | 2347
2022-03-20 | 2166
2022-03-21 | 1977
2022-03-22 | 1932
2022-03-23 | 2121
2022-03-24 | 2160 | [13 empty] | 26
2022-03-25 | 2373 | [13 empty] | 15
2022-03-26 | 2864
2022-03-27 | 3677 | [13 empty] | 85
2022-03-28 | 4370 | [13 empty] | 100
2022-03-29 | 4199 | [13 empty] | 200
2022-03-30 | 8341
2022-03-31 | 6581
2022-04-01 | 6515
2022-04-02 | 4647 | [13 empty] | 20
2022-04-03 | 4107 | [13 empty] | 15
2022-04-04 | 3762
2022-04-05 | 3185
2022-04-06 | 3324 | 0.86 | 1 | 7 | 28 | 14 | 5 | 3.5 | 0.33 | 16.62 | 11.63 | 3.32 | 1.1 | 46.54 | 15 | Adrian O'Rourke | 9.30 AM | 2022-06-30 | 2022-06-08
2022-04-07 | 2907 | [13 empty] | 7
2022-04-08 | 3489 | [13 empty] | 22
2022-04-09 | 3080
2022-04-10 | 2785
2022-04-11 | 2674 | [13 empty] | 10
2022-04-12 | 2531 | 0.45 | 1 | 7 | 1 | 3 | 1 | 2.7 | 0.12 | 2.53 | 6.83 | 2.53 | 0.3 | 7.59 |  | Adrian O'Rourke | 08.30 AM | 2022-06-08 | 2022-06-08
2022-04-13 | 1942 | [13 empty] | 5
2022-04-14 | 3046 | [13 empty] | 12
2022-04-15 | 2629 | [13 empty] | 4
2022-04-16 | 2759
2022-04-17 | 2394
2022-04-18 | 2622
2022-04-19 | 2245
2022-04-20 | 2016
2022-04-21 | 2394
2022-04-22 | 1893
2022-04-23 | 2119 | [13 empty] | 30
2022-04-24 | 2115
2022-04-25 | 1785 | [13 empty] | 10
2022-04-26 | 1990 | 0.66 | 1 | 7 | 2 | 4 | 3 | 5 | 0.15 | 5.97 | 9.95 | 1.99 | 0.3 | 8.56 | 3 | Adrian O'Rouke | 08:30AM | 2022-05-25 | 23.06.2022
2022-04-27 | 1970
2022-04-28 | 1975
2022-04-29 | 1606 | [13 empty] | 8
2022-04-30 | 2173 | [13 empty] | 3
2022-05-01 | 1481 | [13 empty] | 20
2022-05-02 | 2463
2022-05-03 | 2037 | [13 empty] | 7
2022-05-04 | 1907
2022-05-05 | 1972
2022-05-06 | 2017
2022-05-07 | 2089
2022-05-08 | 2308
2022-05-09 | 2543
2022-05-10 | 1783
2022-05-11 | 1882 | 0.43 | 1 | 7.3 | 5 | 4 | 3 | 3.3 | 0.12 | 5.65 | 3.3 | 1.88 | 0.23 | 7.53 |  | Adrian O'Rourke | 10:00am | 21.6.2022 | 23.06.2022
2022-05-12 | 2226 | [13 empty] | 6
2022-05-13 | 1591 | [13 empty] | 2
2022-05-14 | 1839 | [13 empty] | 13
2022-05-15 | 1851 | [13 empty] | 28
2022-05-16 | 2535
2022-05-17 | 2291
2022-05-18 | 1652
2022-05-19 | 1863
2022-05-20 | 1859 | [13 empty] | 4
2022-05-21 | 1718 | [13 empty] | 32
2022-05-22 | 2319
2022-05-23 | 2952 | [13 empty] | 80
2022-05-24 | 3184 | [13 empty] | 20
2022-05-25 | 3713 | 0.42 | 1 | 7.2 | 3 | 7 | 2 | 3.3 | 0.21 | 7.43 | 12.25 | 3.71 | 0.78 | 25.99 | 23 | David Cash | 0.42708 | 2022-06-22 | 2022-06-23
2022-05-26 | 2851 | [13 empty] | 10
2022-05-27 | 2827 | [13 empty] | 6
2022-05-28 | 2325
2022-05-29 | 2544 | [13 empty] | 8
2022-05-30 | 2393
2022-05-31 | 1868
MINIMUM | 697 | 0.35 | 0.01 | 6.7 | 1 | 1 | 1 | 1.9 | 0.04 | 0.55 | 3.3 | 0.94 | 0.08 | 1.58 | 15
AVERAGE | 1876.4222 | 0.68192 | 0.34708 | 7.21 | 747.2778 | 9.2308 | 3.15 | 3.9423 | 0.23885 | 6.3267 | 7.4492 | 2.3257 | 0.64261 | 26.1601 | 4.3648
MAXIMUM | 8343 | 2.2 | 2 | 7.5 | 13000 | 97 | 16 | 7.7 | 2.1 | 68.16 | 32.8 | 8.52 | 8.95 | 413.22 | 107
| Sample Count | 26 | [6 empty] | Total | 171.3707 | 204.4272 | 63.7327 | 17.4304 | 707.9021 | 1180.8648

## 22-23
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 22/23
EPA Licence Number: 2386 - Broadwater Road Evans Head
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Sampled By | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - |  | - | - | -
2022-06-01 | 2136 | [13 empty] | 0
2022-06-02 | 1924 | [13 empty] | 0
2022-06-03 | 1485 | [13 empty] | 0
2022-06-04 | 1843 | [13 empty] | 16
2022-06-05 | 1923 | [13 empty] | 0
2022-06-06 | 1711 | [13 empty] | 2
2022-06-07 | 2029 | [13 empty] | 0
2022-06-08 | 1735 | 0.4 | 1 | 6.8 | 1 | 2 | 1 | 4.1 | 0.09 | 1.64 | 6.71 | 1.64 | 0.14 | 3.27 | 0 | Adrian O'Rourke | 7:15 | 2022-06-26 | 2022-06-26
2022-06-09 | 1637 | [13 empty] | 0
2022-06-10 | 1396 | [13 empty] | 0
2022-06-11 | 1392 | [13 empty] | 0
2022-06-12 | 1831 | [13 empty] | 0
2022-06-13 | 1528 | [13 empty] | 0
2022-06-14 | 1535 | [13 empty] | 0
2022-06-15 | 1262 | [13 empty] | 0
2022-06-16 | 1484 | [13 empty] | 0
2022-06-17 | 1451 | [13 empty] | 0
2022-06-18 | 1643 | [13 empty] | 0
2022-06-19 | 1296 | [13 empty] | 0
2022-06-20 | 1430 | [13 empty] | 3
2022-06-21 | 1477 | [13 empty] | 5
2022-06-22 | 1479 | [13 empty] | 0
2022-06-23 | 1226 | [13 empty] | 0
2022-06-24 | 1631 | [13 empty] | 0
2022-06-25 | 1420 | [13 empty] | 0
2022-06-26 | 1422 | [13 empty] | 0
2022-06-27 | 1223 | 0.64 | 1 | 7.2 | 1 | 3 | 2 | 3.8 | 0.088 | 2.96 | 5.62 | 1.48 | 0.13 | 4.44 |  | David Cash | 10:15 | 2022-07-13 | 2022-07-13
2022-06-28 | 1521 | [13 empty] | 0
2022-06-29 | 1796 | [13 empty] | 0
2022-06-30 | 1486 | [13 empty] | 0
2022-07-01 | 1062 | [13 empty] | 0
2022-07-02 | 1546 | [13 empty] | 20
2022-07-03 | 1801 | [13 empty] | 4
2022-07-04 | 1854 | [13 empty] | 0
2022-07-05 | 1334 | [13 empty] | 8
2022-07-06 | 2012 | 0.6 | 2 | 7.2 | 1 | 7 | 4 | 3.6 | 0.14 | 9.4 | 8.46 | 4.7 | 0.33 | 16.46 | 18 | Adrian O'Rourke | 7:15 | 2022-07-15 | 2022-07-20
2022-07-07 | 2351 | [13 empty] | 7
2022-07-08 | 1884 | [13 empty] | 0
2022-07-09 | 1813 | [13 empty] | 0
2022-07-10 | 2042 | [13 empty] | 0
2022-07-11 | 1438 | [13 empty] | 0
2022-07-12 | 1764 | [13 empty] | 0
2022-07-13 | 1357 | [13 empty] | 2
2022-07-14 | 1518 | [13 empty] | 0
2022-07-15 | 1699 | [13 empty] | 0
2022-07-16 | 1296 | [13 empty] | 0
2022-07-17 | 1426 | [13 empty] | 0
2022-07-18 | 1658 | [13 empty] | 0
2022-07-19 | 1266 | 0.64 | 2 | 7 | 1 | 8 | 2 | 4.6 | 0.28 | 2.53 | 5.82 | 2.53 | 0.35 | 10.13 | 24 | Adrian O'Rouke | 11:15 | 2022-08-01 | 2022-08-01
2022-07-20 | 1971 | [13 empty] | 8
2022-07-21 | 1926 | [13 empty] | 2
2022-07-22 | 1507 | [13 empty] | 13
2022-07-23 | 2425 | [13 empty] | 5
2022-07-24 | 1822 | [13 empty] | 3
2022-07-25 | 1883 | [13 empty] | 3
2022-07-26 | 1528 | [13 empty] | 0
2022-07-27 | 1362 | [13 empty] | 0
2022-07-28 | 1843 | [13 empty] | 0
2022-07-29 | 1642 | [13 empty] | 0
2022-07-30 | 1799 | [13 empty] | 0
2022-07-31 | 1430 | [13 empty] | 0
2022-08-01 | 1117 | [13 empty] | 0
2022-08-02 | 1656 | [13 empty] | 0
2022-08-03 | 1205 | 0.61 | 2 | 7.2 | 1 | 5 | 2 | 3.5 | 0.14 | 2.41 | 4.22 | 2.41 | 0.17 | 5.42 | 0 | Adrian O'Rouke | 9:30 | 2022-08-15 | 2022-08-18
2022-08-04 | 1357 | [13 empty] | 0
2022-08-05 | 1017 | [13 empty] | 0
2022-08-06 | 1833 | [13 empty] | 0
2022-08-07 | 1192 | [13 empty] | 2
2022-08-08 | 1391 | [13 empty] | 0
2022-08-09 | 1081 | [13 empty] | 0
2022-08-10 | 1100 | [13 empty] | 0
2022-08-11 | 1598 | [13 empty] | 0
2022-08-12 | 1180 | [13 empty] | 0
2022-08-13 | 1564 | [13 empty] | 1
2022-08-14 | 938 | [13 empty] | 5
2022-08-15 | 1531 | [13 empty] | 0
2022-08-16 | 1320 | 0.77 | 2 | 7.4 | 1 | 6 | 2 | 2.8 | 0.15 | 2.53 | 3.54 | 2.53 | 0.19 | 7.59 | 0 | Adrian O'Rouke | 10:30 | 2022-08-26 | 2022-08-30
2022-08-17 | 1161 | [13 empty] | 2
2022-08-18 | 1265 | [13 empty] | 0
2022-08-19 | 1180 | [13 empty] | 0
2022-08-20 | 1177 | [13 empty] | 0
2022-08-21 | 1347 | [13 empty] | 0
2022-08-22 | 776 | [13 empty] | 0
2022-08-23 | 990 | [13 empty] | 0
2022-08-24 | 1564 | [13 empty] | 3
2022-08-25 | 1280 | [13 empty] | 0
2022-08-26 | 1181 | [13 empty] | 0
2022-08-27 | 980 | [13 empty] | 0
2022-08-28 | 1565 | [13 empty] | 7
2022-08-29 | 781 | [13 empty] | 3
2022-08-30 | 1769 | 1.1 | 2 | 7 | 1 | 4 | 2 | 3.8 | 0.13 | 3.54 | 6.72 | 3.54 | 0.23 | 7.08 | 1 | Adrian O'Rouke | 10:00 | 2022-09-19 | 2022-09-21
2022-08-31 | 1023 | [13 empty] | 5
2022-09-01 | 1402 | [13 empty] | 0
2022-09-02 | 1342 | [13 empty] | 0
2022-09-03 | 1165 | [13 empty] | 0
2022-09-04 | 2406 | [13 empty] | 22
2022-09-05 | 2463 | [13 empty] | 67
2022-09-06 | 1837 | [13 empty] | 8
2022-09-07 | 1519 | [13 empty] | 2
2022-09-08 | 1622 | [13 empty] | 0
2022-09-09 | 1608 | [13 empty] | 0
2022-09-10 | 1593 | [13 empty] | 0
2022-09-11 | 1749 | [13 empty] | 0
2022-09-12 | 1426 | [13 empty] | 0
2022-09-13 | 1199 | 0.64 | <2 | 7.1 | 3 | 6.5 | <2 | 4 | 0.17 | 1.43 | 5.7 | 1.43 | 0.24 | 9.27 | 0 | Adrian O'Rourke | 7:30 | 2022-09-27 | 2022-10-04
2022-09-14 | 1407 | [13 empty] | 3
2022-09-15 | 1565 | [13 empty] | 0
2022-09-16 | 1283 | [13 empty] | 4
2022-09-17 | 1584 | [13 empty] | 4
2022-09-18 | 1260 | [13 empty] | 0
2022-09-19 | 1162 | [13 empty] | 0
2022-09-20 | 1191 | [13 empty] | 0
2022-09-21 | 1403 | [13 empty] | 0
2022-09-22 | 1607 | [13 empty] | 9
2022-09-23 | 2337 | [13 empty] | 60
2022-09-24 | 2728 | [13 empty] | 16
2022-09-25 | 2173 | [13 empty] | 0
2022-09-26 | 1601 | [13 empty] | 0
2022-09-27 | 1538 | 0.84 | <2 | 6.9 | 4 | 7 | <2 | 2.9 | 0.19 | 1.54 | 4.46 | 1.54 | 0.29 | 10.77 | 0 | Adrian O'Rouke | 9:30 | 2022-10-10 | 2022-10-12
2022-09-28 | 2070 | [13 empty] | 0
2022-09-29 | 1712 | [13 empty] | 1
2022-09-30 | 1625 | [13 empty] | 0
2022-10-01 | 2229 | [13 empty] | 0
2022-10-02 | 2229 | [13 empty] | 3
2022-10-03 | 2229 | [13 empty] | 40
2022-10-04 | 2145 | [13 empty] | 0
2022-10-05 | 1779 | [13 empty] | 0
2022-10-06 | 1820 | [13 empty] | 2
2022-10-07 | 1514 | [13 empty] | 0
2022-10-08 | 1810 | [13 empty] | 0
2022-10-09 | 1367 | [13 empty] | 7
2022-10-10 | 1532 | [13 empty] | 22
2022-10-11 | 1489 | 1.1 | <2 | 7.3 | 1 | 7 | <2 | 3 | 0.21 | 1.53 | 4.6 | 1.53 | 0.32 | 9.96 | 12 | Adrian O'Rourke | 10:00 | 2022-10-26 | 2022-10-26
2022-10-12 | 1422 | [13 empty] | 4
2022-10-13 | 1902 | [13 empty] | 0
2022-10-14 | 1531 | [13 empty] | 0
2022-10-15 | 1742 | [13 empty] | 2
2022-10-16 | 1350 | [13 empty] | 0
2022-10-17 | 1052 | [13 empty] | 3
2022-10-18 | 774 | [13 empty] | 12
2022-10-19 | 1840 | [13 empty] | 0
2022-10-20 | 1461 | [13 empty] | 5
2022-10-21 | 1426 | [13 empty] | 5
2022-10-22 | 1747 | [13 empty] | 2
2022-10-23 | 1742 | [13 empty] | 7
2022-10-24 | 1628 | [13 empty] | 121
2022-10-25 | 3731 | 0.58 | <2 | 7.1 | 4 | 10 | <2 | 2.4 | 0.27 | 4.88 | 3.91 | 1.63 | 0.44 | 16.28 | 7 | Adrian O'Rourke | 7:00 | 2022-11-09 | 2022-11-09
2022-10-26 | 4947 | [13 empty] | 0
2022-10-27 | 2920 | [13 empty] | 0
2022-10-28 | 2282 | [13 empty] | 0
2022-10-29 | 2379 | [13 empty] | 0
2022-10-30 | 1855 | [13 empty] | 0
2022-10-31 | 2321 | [13 empty] | 0
2022-11-01 | 1737 | [13 empty] | 0
2022-11-02 | 1931 | [13 empty] | 8
2022-11-03 | 1907 | [13 empty] | 0
2022-11-04 | 1794 | [13 empty] | 0
2022-11-05 | 1194 | [13 empty] | 3
2022-11-06 | 1824 | [13 empty] | 6
2022-11-07 | 1455 | [13 empty] | 8
2022-11-08 | 1450 | 1 | <2 | 6.9 | 1 | 7 | 3 | 3.3 | 0.18 | 3.64 | 4.8 | 1.46 | 0.26 | 10.19 | 0 | Adrian O'Rourke | 8:30 | 2022-11-17 | 2022-11-21
2022-11-09 | 1764 | [13 empty] | 11
2022-11-10 | 1330 | [13 empty] | 0
2022-11-11 | 1507 | [13 empty] | 0
2022-11-12 | 1585 | [13 empty] | 0
2022-11-13 | 1596 | [13 empty] | 0
2022-11-14 | 1047 | [13 empty] | 0
2022-11-15 | 1554 | [13 empty] | 0
2022-11-16 | 1589 | [13 empty] | 0
2022-11-17 | 1318 | [13 empty] | 0
2022-11-18 | 1394 | [13 empty] | 0
2022-11-19 | 1288 | [13 empty] | 0
2022-11-20 | 1059 | [13 empty] | 0
2022-11-21 | 1566 | 0.78 | 1 | 7.1 | 0 | 8 | 1 | 3.9 | 0.15 | 1.05 | 4.13 | 1.06 | 0.16 | 8.47 | 0 | Adrian O'Rourke | 14:00 | 2022-12-07 | 2022-12-09
2022-11-22 | 1223 | [13 empty] | 0
2022-11-23 | 1630 | [13 empty] | 0
2022-11-24 | 1149 | [13 empty] | 0
2022-11-25 | 901 | [13 empty] | 0
2022-11-26 | 1565 | [13 empty] | 0
2022-11-27 | 1265 | [13 empty] | 0
2022-11-28 | 1171 | [13 empty] | 0
2022-11-29 | 1439 | [13 empty] | 0
2022-11-30 | 1132 | [13 empty] | 0
2022-12-01 | 872 | [13 empty] | 9
2022-12-02 | 760 | [13 empty] | 27
2022-12-03 | 1413 | [13 empty] | 0
2022-12-04 | 1941 | [13 empty] | 3
2022-12-05 | 1317 | 1 | <2 | 7 | 0 | 1 | <2 | 4 | 0 | 1.94 | 7.96 | 1.94 | 0.25 | 1.94 | 7 | Adrian O'Rouke | 8:30 | 2023-12-21 | 2023-01-04
2022-12-06 | 1466 | [13 empty] | 7
2022-12-07 | 1508 | [13 empty] | 0
2022-12-08 | 1319 | [13 empty] | 0
2022-12-09 | 1324 | [13 empty] | 0
2022-12-10 | 1350 | [13 empty] | 0
2022-12-11 | 1129 | [13 empty] | 4
2022-12-12 | 951 | [13 empty] | 0
2022-12-13 | 1115 | [13 empty] | 0
2022-12-14 | 1441 | [13 empty] | 5
2022-12-15 | 1459 | [13 empty] | 0
2022-12-16 | 1254 | [13 empty] | 0
2022-12-17 | 1135 | [13 empty] | 0
2022-12-18 | 1245 | [13 empty] | 0
2022-12-19 | 764 | [13 empty] | 0
2022-12-20 | 1156 | 1 | <2 | 7 | 3 | 10 | NT | 4 | 0 |  | 3.06 |  | 0.23 | 7.64 | 0 | David Cash | 8:30 | 2023-01-12 | 2023-01-16
2022-12-21 | 1759 | [13 empty] | 0
2022-12-22 | 989 | [13 empty] | 0
2022-12-23 | 1322 | [13 empty] | 0
2022-12-24 | 1269 | [13 empty] | 0
2022-12-25 | 1455 | [13 empty] | 0
2022-12-26 | 1208 | [13 empty] | 2
2022-12-27 | 1248 | [13 empty] | 0
2022-12-28 | 1232 | [13 empty] | 0
2022-12-29 | 1480 | [13 empty] | 0
2022-12-30 | 1597 | [13 empty] | 3
2022-12-31 | 1020 | [13 empty] | 0
2023-01-01 | 1605 | [13 empty] | 0
2023-01-02 | 1133 | [13 empty] | 1
2023-01-03 | 1491 | 1.1 | 1 | 6.9 | 2 | 10 | 2.6 | 6 | 0.24 | 2.9 | 6.8 | 1.1 | 0.27 | 11 | 1 | David Cash | 7.45 AM | 2023-01-16 | 2023-03-24
2023-01-04 | 1491 | [13 empty] | 0
2023-01-05 | 1050 | [13 empty] | 0
2023-01-06 | 1954 | [13 empty] | 16
2023-01-07 | 1447 | [13 empty] | 30
2023-01-08 | 1452 | [13 empty] | 0
2023-01-09 | 1404 | [13 empty] | 4
2023-01-10 | 1308 | [13 empty] | 0
2023-01-11 | 1319 | [13 empty] | 0
2023-01-12 | 1604 | [13 empty] | 0
2023-01-13 | 963 | [13 empty] | 0
2023-01-14 | 1784 | [13 empty] | 0
2023-01-15 | 1313 | [13 empty] | 0
2023-01-16 | 1209 | 0.69 | 1 | 7 | 3 | 6 | 2.9 | 6.1 | 0.16 | 3.8 | 8 | 1.3 | 0.21 | 7 | 0 | David Cash | 14:30 | 2023-01-30 | 2023-03-24
2023-01-17 | 799 | [13 empty] | 0
2023-01-18 | 1717 | [13 empty] | 0
2023-01-19 | 814 | [13 empty] | 0
2023-01-20 | 1501 | [13 empty] | 0
2023-01-21 | 1656 | [13 empty] | 36
2023-01-22 | 1233 | [13 empty] | 2
2023-01-23 | 1324 | [13 empty] | 2
2023-01-24 | 1069 | [13 empty] | 0
2023-01-25 | 845 | [13 empty] | 0
2023-01-26 | 1558 | [13 empty] | 7
2023-01-27 | 1346 | [13 empty] | 0
2023-01-28 | 1182 | [13 empty] | 0
2023-01-29 | 1257 | [13 empty] | 0
2023-01-30 | 1172 | 0.38 | 1 | 7.3 | 4 | 6 | 2.4 | 4.3 | 0.19 | 3 | 5.4 | 2.5 | 0.24 | 8 | 0 | David Cash | 15:45 | 2023-02-10 | 2023-03-24
2023-01-31 | 1122 | [13 empty] | 17
2023-02-01 | 1573 | [13 empty] | 44
2023-02-02 | 1669 | [13 empty] | 0
2023-02-03 | 1135 | [13 empty] | 0
2023-02-04 | 1438 | [13 empty] | 0
2023-02-05 | 1236 | [13 empty] | 0
2023-02-06 | 1263 | [13 empty] | 0
2023-02-07 | 1231 | [13 empty] | 0
2023-02-08 | 1122 | [13 empty] | 0
2023-02-09 | 1159 | [13 empty] | 0
2023-02-10 | 1303 | [13 empty] | 0
2023-02-11 | 1010 | [13 empty] | 0
2023-02-12 | 1261 | [13 empty] | 0
2023-02-13 | 1286 | 0.66 | <2 | 7.1 | 5 | 5 | 2.1 | 4.4 | 0.19 | 2.6 | 5.5 | 2.5 | 0.24 | 6 | 0 | Rebekah McLelland | 10:27 | 2023-02-22 | 2023-03-24
2023-02-14 | 1124 | [13 empty] | 0
2023-02-15 | 1216 | [13 empty] | 27
2023-02-16 | 1546 | [13 empty] | 0
2023-02-17 | 1546 | [13 empty] | 0
2023-02-18 | 1196 | [13 empty] | 0
2023-02-19 | 1264 | [13 empty] | 0
2023-02-20 | 857 | [13 empty] | 0
2023-02-21 | 1326 | [13 empty] | 0
2023-02-22 | 1207 | [13 empty] | 6
2023-02-23 | 1028 | [13 empty] | 5
2023-02-24 | 1398 | [13 empty] | 18
2023-02-25 | 1109 | [13 empty] | 0
2023-02-26 | 1282 | [13 empty] | 0
2023-02-27 | 1163 | 0.34 | <2 | 7 | 23 | 26 | 5.2 | 7 | 0.89 | 6.6664 | 8.974 |  | 1.141 | 33.332 | 4 | Rebekah McLelland | 13:50 | 2023-03-09 | 2023-03-24
2023-02-28 | 1347 | [13 empty] | 0
2023-03-01 | 1146 | [13 empty] | 0
2023-03-02 | 570 | [13 empty] | 14
2023-03-03 | 1487 | [13 empty] | 14
2023-03-04 | 1227 | [13 empty] | 6
2023-03-05 | 1140 | [13 empty] | 0
2023-03-06 | 1315 | [13 empty] | 0
2023-03-07 | 709 | [13 empty] | 0
2023-03-08 | 1577 | [13 empty] | 0
2023-03-09 | 1102 | [13 empty] | 0
2023-03-10 | 1143 | [13 empty] | 0
2023-03-11 | 1075 | [13 empty] | 1
2023-03-12 | 826 | [13 empty] | 0
2023-03-13 | 1457 | [13 empty] | 26
2023-03-14 | 996 | 0.6 | <2 | 6.9 | 1 | 3 | 2 | 4 | 0.27 | 1.99 | 3.98 | 2.9 | 0.27 | 2.99 | 26 | Paul Gibson | 10:30 | 2023-03-24 | 2023-03-24
2023-03-15 | 1500 | [13 empty] | 0
2023-03-16 | 997 | [13 empty] | 0
2023-03-17 | 1142 | [13 empty] | 0
2023-03-18 | 1156 | [13 empty] | 0
2023-03-19 | 1039 | [13 empty] | 0
2023-03-20 | 1115 | [13 empty] | 0
2023-03-21 | 975 | [13 empty] | 0
2023-03-22 | 1314 | [13 empty] | 0
2023-03-23 | 941 | [13 empty] | 8
2023-03-24 | 1009 | [13 empty] | 0
2023-03-25 | 1436 | [13 empty] | 0
2023-03-26 | 878 | [13 empty] | 0
2023-03-27 | 1204 | [13 empty] | 3
2023-03-28 | 1294 | 0.51 | <2 | 7.1 | 7 | 3 | 2 | 5.5 | 0.1 | 2.35 | 6.47 | 2.35 | 0.12 | 3.53 | 0 | Rebekah MccLelland | 8:03 | 2023-04-11 | 2023-04-11
2023-03-29 | 1176 | [13 empty] | 0
2023-03-30 | 1177 | [13 empty] | 8
2023-03-31 | 1110 | [13 empty] | 0
2023-04-01 | 1065 | [13 empty] | 0
2023-04-02 | 1127 | [13 empty] | 0
2023-04-03 | 1449 | [13 empty] | 28
2023-04-04 | 998 | [13 empty] | 7
2023-04-05 | 1280 | [13 empty] | 0
2023-04-06 | 1245 | [13 empty] | 0
2023-04-07 | 1362 | [13 empty] | 2
2023-04-08 | 1266 | [13 empty] | 0
2023-04-09 | 1150 | [13 empty] | 0
2023-04-10 | 1682 | [13 empty] | 0
2023-04-11 | 1008 | 0.65 | 1 | 7.2 | 3 | 2 | 2 | 5.3 | 0.66 | 2.22 | 5.34 | 1.01 | 0.09 | 1.51 | 0 | David Cash | 9:00AM | 2023-05-01 | 2023-05-08
2023-04-12 | 1149 | [13 empty] | 0
2023-04-13 | 1243 | [13 empty] | 0
2023-04-14 | 1071 | [13 empty] | 0
2023-04-15 | 1246 | [13 empty] | 0
2023-04-16 | 922 | [13 empty] | 0
2023-04-17 | 1255 | [13 empty] | 3
2023-04-18 | 1073 | [13 empty] | 3
2023-04-19 | 1244 | [13 empty] | 1
2023-04-20 | 921 | [13 empty] | 0
2023-04-21 | 1531 | [13 empty] | 0
2023-04-22 | 1113 | [13 empty] | 0
2023-04-23 | 1079 | [13 empty] | 37
2023-04-24 | 1181 | [13 empty] | 0
2023-04-25 | 1069 | [13 empty] | 0
2023-04-26 | 1069 | [13 empty] | 0
2023-04-27 | 1305 | 0.45 | 1 | 7 | 1 | 5 | 1 | 2.3 | 0.03 | 1.31 | 3 | 1.31 | 0.12 | 6.53 | 0 | David Cash | 8:25
2023-04-28 | 1417 | [13 empty] | 0
2023-04-29 | 1196 | [13 empty] | 0
2023-04-30 | 839 | [13 empty] | 0
2023-05-01 | 1215 | [13 empty] | 0
2023-05-02 | 1193 | [13 empty] | 0
2023-05-03 | 1271 | [13 empty] | 0
2023-05-04 | 1087 | [13 empty] | 0
2023-05-05 | 382 | [13 empty] | 0
2023-05-06 | 1502 | [13 empty] | 0
2023-05-07 | 1091 | [13 empty] | 0
2023-05-08 | 1319 | [13 empty] | 0
2023-05-09 | 1319 | 0.25 | 1 | 7 | 1 | 3 | 1 | 5 | 0.09 | 1.32 | 6.6 | 1.32 | 0.11 | 3.3 | 0 | Paul Gibson | 7:15AM | 2023-05-19 | 2023-06-02
2023-05-10 | 494 | [13 empty] | 0
2023-05-11 | 1311 | [13 empty] | 2
2023-05-12 | 1190 | [13 empty] | 7
2023-05-13 | 1235 | [13 empty] | 5
2023-05-14 | 1134 | [13 empty] | 0
2023-05-15 | 1176 | [13 empty] | 25
2023-05-16 | 2391 | [13 empty] | 35
2023-05-17 | 1655 | [13 empty] | 26
2023-05-18 | 1244 | [13 empty] | 0
2023-05-19 | 1554 | [13 empty] | 0
2023-05-20 | 1016 | [13 empty] | 0
2023-05-21 | 1275 | [13 empty] | 0
2023-05-22 | 1248 | [13 empty] | 0
2023-05-23 | 1209 | 0.28 | 1 | 7 | 1 | 3 | 1 | 3.8 | 0.09 | 1.21 | 4.59 | 1.21 | 0.1 | 3.02 | 0 | Paul Gibson | 8:00 | 2023-06-01 | 2023-06-02
2023-05-24 | 1225 | [13 empty] | 0
2023-05-25 | 818 | [13 empty] | 0
2023-05-26 | 1654 | [13 empty] | 0
2023-05-27 | 1056 | [13 empty] | 0
2023-05-28 | 1235 | [13 empty] | 0
2023-05-29 | 1169 | [13 empty] | 0
2023-05-30 | 1141 | [13 empty] | 0
2023-05-31 | 1158 | [13 empty] | 0
MINIMUM | 382 | 0.25 | 1 | 6.8 | 0 | 1 | 1 | 2.3 | 0 | 1.05 | 3 | 1.01 | 0.09 | 1.51 | 15
AVERAGE | 1415.8736 | 0.7263 | 1.375 | 7.0654 | 10.1481 | 6.6111 | 2.5333 | 4.3481 | 0.19993 | 2.8155 | 5.5525 | 1.955 | 0.25542 | 8.2739 | 3.3939
MAXIMUM | 4947 | 2 | 2 | 7.4 | 200 | 26 | 10 | 10 | 0.89 | 9.4 | 8.974 | 4.7 | 1.141 | 33.332 | 121
| Sample Count | 26 | [6 empty] | Total | 83.6519 | 161.8905 | 54.585 | 8.1274 | 258.2379 | 1355.3939

## 23-24
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 23/24
EPA Licence Number: 2386 - Broadwater Road Evans Head
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Sampled By | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - |  | - | - | -
2023-06-01 | 1144 | [13 empty] | 0
2023-06-02 | 809 | [13 empty] | 0
2023-06-03 | 1362 | [13 empty] | 0
2023-06-04 | 948 | [13 empty] | 0
2023-06-05 | 739 | [13 empty] | 4
2023-06-06 | 1579 | 0.51 | 1 | 7.1 | 1 | 0.5 | 1 | 4 | 0.1 | 1 | 3.81 | 0.95 | 0.09 | 0.48 | 6 | Rebekah McClelland | 10:20AM | 2023-06-19 | 2023-07-10
2023-06-07 | 953 | [13 empty] | 5
2023-06-08 | 1416 | [13 empty] | 0
2023-06-09 | 1010 | [13 empty] | 0
2023-06-10 | 1168 | [13 empty] | 0
2023-06-11 | 1279 | [13 empty] | 0
2023-06-12 | 1006 | [13 empty] | 0
2023-06-13 | 961 | [13 empty] | 0
2023-06-14 | 1293 | [13 empty] | 0
2023-06-15 | 1058 | [13 empty] | 0
2023-06-16 | 1075 | [13 empty] | 0
2023-06-17 | 898 | [13 empty] | 0
2023-06-18 | 811 | [13 empty] | 0
2023-06-19 | 1581 | [13 empty] | 0
2023-06-20 | 817 | 0.23 | 1 | 6.8 | 0.5 | 3.5 | 1 | 3.8 | 0.08 | 1.1 | 4.02 | 1.06 | 0.08 | 3.7 | 0 | Adriano Martinez | 8:00AM | 2023-06-30 | 2023-07-10
2023-06-21 | 961 | [13 empty] | 0
2023-06-22 | 1469 | [13 empty] | 0
2023-06-23 | 1020 | [13 empty] | 0
2023-06-24 | 1224 | [13 empty] | 0
2023-06-25 | 594 | [13 empty] | 0
2023-06-26 | 1446 | [13 empty] | 0
2023-06-27 | 1286 | [13 empty] | 0
2023-06-28 | 1110 | [13 empty] | 0
2023-06-29 | 1089 | [13 empty] | 0
2023-06-30 | 1101 | [13 empty] | 0
2023-07-01 | 952 | [13 empty] | 0
2023-07-02 | 1262 | [13 empty] | 0
2023-07-03 | 773 | 0.59 | 1 | 7.2 | 2 | 2.5 | 1 | 4.4 | 0.08 | 1.1 | 4.88 | 1.11 | 0.09 | 2.78 | 4 | Rebekah McClelland | 3:00PM | 2023-07-14 | 2023-07-25
2023-07-04 | 1523 | [13 empty] | 3
2023-07-05 | 795 | [13 empty] | 6
2023-07-06 | 1466 | [13 empty] | 0
2023-07-07 | 1466 | [13 empty] | 0
2023-07-08 | 1138 | [13 empty] | 0
2023-07-09 | 804 | [13 empty] | 0
2023-07-10 | 1362 | [13 empty] | 0
2023-07-11 | 928 | [13 empty] | 0
2023-07-12 | 1171 | [13 empty] | 0
2023-07-13 | 891 | [13 empty] | 0
2023-07-14 | 1100 | [13 empty] | 0
2023-07-15 | 1033 | [13 empty] | 0
2023-07-16 | 966 | [13 empty] | 0
2023-07-17 | 779 | [13 empty] | 3
2023-07-18 | 1488 | 0.4 | 1 | 7.1 | 1 | 2 | 2 | 4.5 | 0.08 | 2.3 | 5.1 | 1.1 | 0.09 | 2 | 0 | Paul Gibson | 7:00AM | 2023-07-27 | 2023-08-25
2023-07-19 | 1130 | [13 empty] | 0
2023-07-20 | 1100 | [13 empty] | 0
2023-07-21 | 963 | [13 empty] | 0
2023-07-22 | 1137 | [13 empty] | 0
2023-07-23 | 969 | [13 empty] | 0
2023-07-24 | 803 | [13 empty] | 0
2023-07-25 | 952 | [13 empty] | 4
2023-07-26 | 1264 | [13 empty] | 0
2023-07-27 | 1207 | [13 empty] | 0
2023-07-28 | 1012 | [13 empty] | 0
2023-07-29 | 1006 | [13 empty] | 0
2023-07-30 | 1205 | [13 empty] | 0
2023-07-31 | 969 | [13 empty] | 0
2023-08-01 | 1162 | 0.26 | 1 | 7.7 | 50 | 1 | 5 | 5 | 7.9 | 5.2 | 5.8 | 1.2 | 9.18 | 1 | 0 | Adriano Martinez | 3.00PM | 2023-08-11 | 2023-08-31
2023-08-02 | 913 | [13 empty] | 0
2023-08-03 | 1274 | [13 empty] | 0
2023-08-04 | 1052 | [13 empty] | 0
2023-08-05 | 932 | [13 empty] | 0
2023-08-06 | 1107 | [13 empty] | 5
2023-08-07 | 1235 | [13 empty] | 8
2023-08-08 | 1035 | [13 empty] | 5
2023-08-09 | 1161 | [13 empty] | 0
2023-08-10 | 833 | [13 empty] | 0
2023-08-11 | 1347 | [13 empty] | 0
2023-08-12 | 1023 | [13 empty] | 0
2023-08-13 | 1309 | [13 empty] | 0
2023-08-14 | 1156 | [13 empty] | 0
2023-08-15 | 529 | [13 empty] | 0
2023-08-16 | 1359 | 0.36 | 1 | 7.1 | 1 | 2 | 2 | 4.5 | 0.16 | 2.3 | 5.1 | 1.1 | 0.18 | 2 | 0 | Rebekah McClelland | 9.00AM | 2023-08-31 | 2023-08-31
2023-08-17 | 1366 | [13 empty] | 0
2023-08-18 | 1128 | [13 empty] | 0
2023-08-19 | 1143 | [13 empty] | 0
2023-08-20 | 1115 | [13 empty] | 0
2023-08-21 | 1122 | [13 empty] | 0
2023-08-22 | 523 | [13 empty] | 0
2023-08-23 | 1196 | [13 empty] | 0
2023-08-24 | 1450 | [13 empty] | 0
2023-08-25 | 1041 | [13 empty] | 0
2023-08-26 | 1056 | [13 empty] | 0
2023-08-27 | 1016 | [13 empty] | 0
2023-08-28 | 480 | [13 empty] | 0
2023-08-29 | 1435 | 0.89 | 1 | 7 | 1 | 5 | 3 | 4.9 | 0.25 | 2.7 | 5 | 1 | 0.25 | 5 | 0 | David Cash | 9.30AM | 2023-09-12 | 2023-05-06
2023-08-30 | 1012 | [13 empty] | 0
2023-08-31 | 1065 | [13 empty] | 0
2023-09-01 | 1162 | [13 empty] | 0
2023-09-02 | 1140 | [13 empty] | 0
2023-09-03 | 1069 | [13 empty] | 0
2023-09-04 | 1121 | [13 empty] | 0
2023-09-05 | 1201 | [13 empty] | 0
2023-09-06 | 1068 | [13 empty] | 0
2023-09-07 | 903 | [13 empty] | 0
2023-09-08 | 1278 | [13 empty] | 0
2023-09-09 | 1123 | [13 empty] | 0
2023-09-10 | 797 | [13 empty] | 0
2023-09-11 | 1170 | [13 empty] | 6
2023-09-12 | 1077 | 0.03 | 1 | 6.9 | 1 | 4 | 2 | 6.8 | 0.4 | 2.1 | 7.3 | 1.1 | 0.43 | 4 | 0 | David Cash | 8.00AM | 2023-09-26 | 2023-05-06
2023-09-13 | 1047 | [13 empty] | 0
2023-09-14 | 762 | [13 empty] | 0
2023-09-15 | 1219 | [13 empty] | 0
2023-09-16 | 821 | [13 empty] | 0
2023-09-17 | 1084 | [13 empty] | 0
2023-09-18 | 1307 | [13 empty] | 0
2023-09-19 | 1278 | [13 empty] | 0
2023-09-20 | 639 | [13 empty] | 0
2023-09-21 | 1252 | [13 empty] | 0
2023-09-22 | 1150 | [13 empty] | 0
2023-09-23 | 1250 | [13 empty] | 0
2023-09-24 | 1130 | [13 empty] | 0
2023-09-25 | 1049 | [13 empty] | 2
2023-09-26 | 1184 | 0.94 | 1 | 7.1 | 1 | 4 | 2 | 5.7 | 0.27 | 2.3 | 6.7 | 1.2 | 0.32 | 4 | 0 | David Cash | 10.00AM | 2023-10-05 | 2023-10-06
2023-09-27 | 1170 | [13 empty] | 0
2023-09-28 | 1178 | [13 empty] | 0
2023-09-29 | 1230 | [13 empty] | 0
2023-09-30 | 1171 | [13 empty] | 0
2023-10-01 | 1171 | [13 empty] | 0
2023-10-02 | 1178 | [13 empty] | 0
2023-10-03 | 1080 | [13 empty] | 0
2023-10-04 | 1017 | [13 empty] | 0
2023-10-05 | 1004 | [13 empty] | 0
2023-10-06 | 677 | [13 empty] | 0
2023-10-07 | 1270 | [13 empty] | 0
2023-10-08 | 974 | [13 empty] | 0
2023-10-09 | 1094 | [13 empty] | 16
2023-10-10 | 776 | 0.35 | 1 | 7.2 | 1 | 4 | 1 | 8.4 | 0.21 | 0.8 | 6.5 | 0.8 | 0.16 | 3 | 0 | David Cash | 8:30 | 2023-10-19 | 2023-11-03
2023-10-11 | 1333 | [13 empty] | 0
2023-10-12 | 969 | [13 empty] | -
2023-10-13 | 1027 | [13 empty] | 0
2023-10-14 | 1023 | [13 empty] | 0
2023-10-15 | 1031 | [13 empty] | 0
2023-10-16 | 796 | [13 empty] | 0
2023-10-17 | 1221 | [13 empty] | 0
2023-10-18 | 978 | [13 empty] | 2
2023-10-19 | 1034 | [13 empty] | 2
2023-10-20 | 1038 | [13 empty] | 0
2023-10-21 | [14 empty] | 0
2023-10-22 | 1046 | [13 empty] | 0
2023-10-23 | 1049 | 0.46 | 1 | 7.2 | 1 | 4 | 3 | 6.2 | 0.33 | 3.1 | 6.5 | 1 | 0.35 | 4 | 0 | Stephen Scott | 14:20 | 2023-11-03 | 2023-11-06
2023-10-24 | 1045 | [13 empty] | 0
2023-10-25 | 933 | [13 empty] | 0
2023-10-26 | 530 | [13 empty] | 0
2023-10-27 | 1508 | [13 empty] | 55
2023-10-28 | 1876 | [13 empty] | 0
2023-10-29 | 1708 | [13 empty] | 0
2023-10-30 | 1155 | [13 empty] | 50
2023-10-31 | 465 | [13 empty] | 0
2023-11-01 | 1467 | [13 empty] | 0
2023-11-02 | 1362 | [13 empty] | 0
2023-11-03 | 1234 | [13 empty] | 0
2023-11-04 | 1297 | [13 empty] | 0
2023-11-05 | 1909 | [13 empty] | 0
2023-11-06 | 2699 | 1.5 | 1 | 7.2 | 2 | 18 | 6 | 7.1 | 0.4 | 15.7 | 19.2 | 2.7 | 1.08 | 49 | 180 | Stephen Scott | 13:40 | 2023-11-20 | 2023-11-20
2023-11-07 | 1872 | [13 empty] | 16
2023-11-08 | 1728 | [13 empty] | 0
2023-11-09 | 2019 | [13 empty] | 0
2023-11-10 | 1391 | [13 empty] | 0
2023-11-11 | 1737 | [13 empty] | 0
2023-11-12 | 1493 | [13 empty] | 0
2023-11-13 | 1484 | [13 empty] | 0
2023-11-14 | 1711 | [13 empty] | 0
2023-11-15 | 1396 | [13 empty] | 0
2023-11-16 | 1268 | [13 empty] | 0
2023-11-17 | 2172 | [13 empty] | 1
2023-11-18 | 2145 | [13 empty] | 10
2023-11-19 | 2669 | [13 empty] | 0
2023-11-20 | 2796 | [13 empty] | 0
2023-11-21 | 2320 | 0.5 | 1 | 6.9 | <1 | 3 | 2 | 6.9 | 0.1 | 6.15 | 19.29 | 2.8 | 0.34 | 9.51 | 12.5 | Rebekah McClelland | 8:55 | 2023-12-06 | 2023-12-15
2023-11-22 | 2300 | [13 empty] | 0
2023-11-23 | 2337 | [13 empty] | 0
2023-11-24 | 2087 | [13 empty] | 4
2023-11-25 | 2129 | [13 empty] | 0
2023-11-26 | 2293 | [13 empty] | 0
2023-11-27 | 3234 | [13 empty] | 0
2023-11-28 | 2740 | [13 empty] | 3
2023-11-29 | 2571 | [13 empty] | 12
2023-11-30 | 2193 | [13 empty] | 1
2023-12-01 | 2077 | [13 empty] | 0
2023-12-02 | 2120 | [13 empty] | 0
2023-12-03 | 2202 | [13 empty] | 0
2023-12-04 | 2224 | [13 empty] | 0
2023-12-05 | 2210 | 0.26 | 1 | 7.2 | <1 | 4 | 1 | 8.9 | 0.3 | 2.22 | 19.79 | 2.22 | 0.73 | 8.9 | 0 | David Cash | 7:30 | 2023-12-15 | 2023-12-15
2023-12-06 | 2162 | [13 empty] | 0
2023-12-07 | 2071 | [13 empty] | 0
2023-12-08 | 2060 | [13 empty] | 0
2023-12-09 | 2035 | [13 empty] | 0
2023-12-10 | 2134 | [13 empty] | 0
2023-12-11 | 2151 | [13 empty] | 0
2023-12-12 | 2180 | [13 empty] | 0
2023-12-13 | 2178 | [13 empty] | 0
2023-12-14 | 1098 | [13 empty] | 0
2023-12-15 | 953 | [13 empty] | 8
2023-12-16 | 1266 | [13 empty] | 0
2023-12-17 | 1093 | [13 empty] | 0
2023-12-18 | 1423 | [13 empty] | 0
2023-12-19 | 1231 | [13 empty] | 0
2023-12-20 | 695 | [13 empty] | 0
2023-12-21 | 1571 | [13 empty] | 0
2023-12-22 | 921 | [13 empty] | 4
2023-12-23 | 1193 | [13 empty] | 0
2023-12-24 | 1096 | [13 empty] | 8
2023-12-25 | 1525 | [13 empty] | 0
2023-12-26 | 812 | [13 empty] | 7
2023-12-27 | 1636 | [13 empty] | 0
2023-12-28 | 1296 | [13 empty] | 0
2023-12-29 | 1254 | [13 empty] | 0
2023-12-30 | 1282 | [13 empty] | 0
2023-12-31 | 1698 | [13 empty] | 0
2024-01-01 | 1194 | 0.6 | 1 | 7.8 | 1 | 2 | 1 | 5.8 | 0.27 | 1.7 | 9.8 | 1.7 | 0.46 | 3 | 8 | David Cash | 10:45AM | 2024-01-15 | 2024-02-28
2024-01-02 | 1418 | [13 empty] | 0
2024-01-03 | 1199 | [13 empty] | 0
2024-01-04 | 1391 | [13 empty] | 1
2024-01-05 | 1417 | [13 empty] | 0
2024-01-06 | 1011 | [13 empty] | 0
2024-01-07 | 1354 | [13 empty] | 0
2024-01-08 | 1150 | [13 empty] | 7
2024-01-09 | 1136 | [13 empty] | 0
2024-01-10 | 1115 | [13 empty] | 0
2024-01-11 | 1417 | [13 empty] | 0
2024-01-12 | 1060 | [13 empty] | 0
2024-01-13 | 1227 | [13 empty] | 0
2024-01-14 | 1189 | [13 empty] | 0
2024-01-15 | 1141 | 0.61 | 1 | 7.3 | 1 | 3.8 | 2.4 | 3.1 | 0.2 | 2.9 | 3.7 | 1.2 | 0.24 | 5 | 15 | Adriano Martinez | 12:10PM | 2024-02-02 | 2024-02-28
2024-01-16 | 1224 | [13 empty] | 29
2024-01-17 | 1568 | [13 empty] | 4
2024-01-18 | 1023 | [13 empty] | 25
2024-01-19 | 1620 | [13 empty] | 0
2024-01-20 | 1244 | [13 empty] | 0
2024-01-21 | 1196 | [13 empty] | 0
2024-01-22 | 1221 | [13 empty] | 5
2024-01-23 | 1134 | [13 empty] | 2
2024-01-24 | 741 | [13 empty] | 0
2024-01-25 | 1476 | [13 empty] | 0
2024-01-26 | 1136 | [13 empty] | 0
2024-01-27 | 1251 | [13 empty] | 0
2024-01-28 | 1481 | [13 empty] | 0
2024-01-29 | 1444 | 0.47 | 1 | 7.8 | 1 | 4.6 | 1 | 3.1 | 0.2 | 1.5 | 4.6 | 1.5 | 0.3 | 7 | 41 | Adriano Martinez | 9:50AM | 2024-02-14 | 2024-02-28
2024-01-30 | 1204 | [13 empty] | 3
2024-01-31 | 990 | [13 empty] | 0
2024-02-01 | 1135 | [13 empty] | 0
2024-02-02 | 702 | [13 empty] | 0
2024-02-03 | 1357 | [13 empty] | 0
2024-02-04 | 1379 | [13 empty] | 0
2024-02-05 | 1178 | [13 empty] | 0
2024-02-06 | 979 | [13 empty] | 0
2024-02-07 | 1108 | [13 empty] | 0
2024-02-08 | 1117 | [13 empty] | 33
2024-02-09 | 1255 | [13 empty] | 17
2024-02-10 | 1586 | [13 empty] | 0
2024-02-11 | 1302 | [13 empty] | 0
2024-02-12 | 1278 | [13 empty] | 29
2024-02-13 | 1375 | 0.15 | 1 | 7.6 | 1 | 5.8 | 2.1 | 3.7 | 0.046 | 2.7 | 4.7 | 1.3 | 0.06 | 7 | 0 | Adriano Martinez | 7:45AM | 2024-02-27 | 2024-02-28
2024-02-14 | 1503 | [13 empty] | 0
2024-02-15 | 1284 | [13 empty] | 0
2024-02-16 | 1054 | [13 empty] | 0
2024-02-17 | 1548 | [13 empty] | 0
2024-02-18 | 1810 | [13 empty] | 0
2024-02-19 | 1451 | [13 empty] | 35
2024-02-20 | 1461 | [13 empty] | 36
2024-02-21 | 1420 | [13 empty] | 0
2024-02-22 | 1551 | [13 empty] | 0
2024-02-23 | 1300 | [13 empty] | 0
2024-02-24 | 1322 | [13 empty] | 0
2024-02-25 | 1272 | [13 empty] | 0
2024-02-26 | 1337 | [13 empty] | 14
2024-02-27 | 1183 | 0.32 | 1 | 7.6 | 1 | 3.4 | 2 | 3.5 | 0.13 | 2.7 | 4.7 | 1.3 | 0.17 | 5 | 0 | Stephen Scott | 7:45AM | 2024-03-11 | 2024-03-13
2024-02-28 | 1252
2024-02-29 | 1312
2024-03-01 | 991
2024-03-02 | 1180
2024-03-03 | 1296
2024-03-04 | 947
2024-03-05 | 1131
2024-03-06 | 1516
2024-03-07 | 1602
2024-03-08 | 1312
2024-03-09 | 1230
2024-03-10 | 978
2024-03-11 | 1332 | 0.35 | 1 | 7.1 | 1 | 5.7 | 1 | 4.1 | 0.12 | 1.33 | 5.46 | 1 | 0.16 | 7.59 |  | Adriano Martinez | 2:25PM | 12.04.2024 | 1.05.2024
2024-03-12 | 1525
2024-03-13 | 1311
2024-03-14 | 1056
2024-03-15 | 1347
2024-03-16 | 874
2024-03-17 | 1640
2024-03-18 | 1524
2024-03-19 | 1519
2024-03-20 | 1492
2024-03-21 | 1282
2024-03-22 | 1919
2024-03-23 | 1687
2024-03-24 | 1473
2024-03-25 | 1596
2024-03-26 | 1304 | 0.41 | 1 | 7.3 | 1 | 6.8 | 2.5 | 4.1 | 0.17 | 5.66 | 9.29 | 2.3 | 0.39 | 15.4 |  | Adriano Martinez | 09:35AM | 30.04.2024 | 1.05.2024
2024-03-27 | 2874
2024-03-28 | 2265
2024-03-29 | 1807
2024-03-30 | 2171
2024-03-31 | 1849
2024-04-01 | 1631
2024-04-02 | 1801
2024-04-03 | 1609
2024-04-04 | 1476
2024-04-05 | 4311
2024-04-06 | 4923
2024-04-07 | 3320
2024-04-08 | 2327
2024-04-09 | 2308 | 0.29 | 1 | 7.4 | 1 | 8.2 | 5.2 | 3.2 | 0.25 | 7.79 | 4.8 | 1.5 | 0.37 | 12.29 |  | Adriano Martinez | 07:50AM | 30.04.2024 | 05.06.2024
2024-04-10 | 2230
2024-04-11 | 1499
2024-04-12 | 1968
2024-04-13 | 1868
2024-04-14 | 1544
2024-04-15 | 1863
2024-04-16 | 1669
2024-04-17 | 1613
2024-04-18 | 1625
2024-04-19 | 1632
2024-04-20 | 2015
2024-04-21 | 3931
2024-04-22 | 3447
2024-04-23 | 2430 | 0.37 | 1 | 7.1 | 4 | 4.5 | 1 | 3 | 0.09 | 0.77 | 6.22 | 2.1 | 0.19 | 9.33 |  | Adriano Martinez | 06:55AM | 14.05.2024 | 05.06.2024
2024-04-24 | 2379
2024-04-25 | 2073
2024-04-26 | 2068
2024-04-27 | 2134
2024-04-28 | 1824
2024-04-29 | 1959
2024-04-30 | 2078
2024-05-01 | 1500
2024-05-02 | 2715
2024-05-03 | 3550
2024-05-04 | 3615
2024-05-05 | 3195
2024-05-06 | 2322
2024-05-07 | 3087 | 0.39 | 1 | 7.1 | 1 | 4.5 | 1 | 4.8 | 0.12 | 2.3 | 11.05 | 2.3 | 0.28 | 10.36 |  | Adriano Martinez | 08:00AM | 23.05.2024 | 05.06.2024
2024-05-08 | 2578
2024-05-09 | 2302
2024-05-10 | 2474
2024-05-11 | 3338
2024-05-12 | 2982
2024-05-13 | 2610
2024-05-14 | 2264
2024-05-15 | 1625
2024-05-16 | 2689
2024-05-17 | 3151
2024-05-18 | 2843
2024-05-19 | 2401
2024-05-20 | 2272
2024-05-21 | 2072 | 0.18 | 1 | 6.9 | 1 | 5.5 | 1 | 4.2 | 0.11 | 2.22 | 9.32 | 2.2 | 0.24 | 12.2 |  | Adriano Martinez | 07:50AM | 04.06.2024 | 05.06.2024
2024-05-22 | 1742
2024-05-23 | 2219
2024-05-24 | 1537
2024-05-25 | 1591
2024-05-26 | 2133
2024-05-27 | 1475
2024-05-28 | 1749
2024-05-29 | 1633
2024-05-30 | 1741
2024-05-31 | 1842
2024-06-01 | 1702
2024-06-02 | 1624
2024-06-03 | 1948 | 0.31 | 1 | 6.7 | 1 | 13 | 3 | 4.2 | 0.1 | 4.15 | 6.7 | 1.6 | 0.16 | 20.75 |  | Adriano Martinez | 07:00AM | 2024-06-26 | 2024-06-26
2024-06-04 | 1596
2024-06-05 | 1352
2024-06-06 | 1792
2024-06-07 | 1318
2024-06-08 | 1729
2024-06-09 | 1354
2024-06-10 | 1533
2024-06-11 | 1506
2024-06-12 | 1271
2024-06-13 | 1661
2024-06-14 | 1402
2024-06-15 | 1340
2024-06-16 | 1491
2024-06-17 | 1567
2024-06-18 | 1378 | 0.45 | 1 | 7 | 1 | 2 | 1 | 4.6 | 0.05 | 1.38 | 6.34 | 1.38 | 0.07 | 2.76 |  | Craig Smith | 8:30am | 2024-07-23
2024-06-19 | 1404
2024-06-20 | 1533
2024-06-21 | 859
2024-06-22 | 1803
2024-06-23 | 1165
2024-06-24 | 1375
2024-06-25 | 1445
2024-06-26 | 1590
2024-06-27 | 1271
2024-06-28 | 1469
2024-06-29 | 1484
2024-06-30 | 1447

## 24-25
EVANS HEAD SEWERAGE TREATMENT PLANT LICENCE REPORTING 23/24
EPA Licence Number: 2386 - Broadwater Road Evans Head
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=72296&sysuid=1&licid=2386
DATE | EPA Point 2 Total volume monitoring (Effluent Pump Flow)) | EPA Point 3 Discharge to waters effluent quality monitoring | [7 empty] | Load Limits | [5 empty] | Sampled By | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | Ammonia | Oil and Grease | pH | Faecal Coliforms | TSS | BOD | TN | TP | BOD (Enclosed waters) | Nitrogen (total) (Enclosed waters) | Oil and Grease (Enclosed waters) | Phosphorus (total) (Enclosed waters) | TSS (Enclosed waters) | Rainfall
| kL/day | mg/L | mg/L |  | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kg | kg | kg | kg | kg | mm
Licence 100 percentile | 6500 | 5 | 6 | 6.5-8.5 | 600 | 30 | 20 | 20 | 1 | 7227 | 9636 | 4818 | 483 | 7227 |  |  | - | - | -
AMT 90 percentile | - | 2 | 2 |  | 200 | 15 | 10 | 10 | 0.3 | - | - | - | - | - | - |  | - | - | -
Monday, 1 July 2024 | 1335 | [13 empty] | 17
Tuesday, 2 July 2024 | 2075 | 1.34 | 1 | 6.7 | 1 | 1 | 1 | 9.63 | 0.08 | 1.27 | 12.24 | 1.27 | 0.1 | 1.27 | 38 | Adriano Martinez | 8:00am | 2024-07-23
Wednesday, 3 July 2024 | 2574 | [13 empty] | 20
Thursday, 4 July 2024 | 2409 | [13 empty] | 20
Friday, 5 July 2024 | 2679 | [13 empty] | 24
Saturday, 6 July 2024 | 2483 | [13 empty] | 0
Sunday, 7 July 2024 | 2687 | [13 empty] | 0
Monday, 8 July 2024 | 2236 | [13 empty] | 27
2024-07-09 | 2128 | [13 empty] | 2
2024-07-10 | 2240 | [13 empty] | 2
2024-07-11 | 1861 | [13 empty] | 0
2024-07-12 | 1677 | [13 empty] | 0
2024-07-13 | 1786 | [13 empty] | 0
2024-07-14 | 1737 | [13 empty] | 0
2024-07-15 | 1891 | [13 empty] | 0
2024-07-16 | 1186 | 1.7 | 1 | 7.1 | 6 | 1 | 1 | 5.81 | 0.07 | 1.19 | 6.89 | 1.19 | 0.08 | 1.19 | 0 | Craig Smith | 8:00am | 2024-07-31
2024-07-17 | 1500 | [13 empty] | 0
2024-07-18 | 1675 | [13 empty] | 0
2024-07-19 | 1358 | [13 empty] | 0
2024-07-20 | 1811 | [13 empty] | 0
2024-07-21 | 1498 | [13 empty] | 0
2024-07-22 | 1466 | [13 empty] | 0
2024-07-23 | 1444 | [13 empty] | 0
2024-07-24 | 1451 | [13 empty] | 0
2024-07-25 | 1454 | [13 empty] | 0
2024-07-26 | 1321 | [13 empty] | 0
2024-07-27 | 1272 | [13 empty] | 0
2024-07-28 | 1651 | [13 empty] | 0
2024-07-29 | 1377 | [13 empty] | 3
2024-07-30 | 1384 | 1.02 | 10 | 7.28 | 310 | 1 | 1.14 | 4.24 | 0.18 | 1.58 | 5.87 | 13.84 | 0.25 | 1.38 | 0 | Garth Cochrane | 11:15am | 2024-08-08
2024-07-31 | 1311 | [13 empty] | 0
2024-08-01 | 1439 | [13 empty] | 0
2024-08-02 | 1405 | [13 empty] | 0
2024-08-03 | 1393 | [13 empty] | 0
2024-08-04 | 1394 | [13 empty] | 0
2024-08-05 | 1374 | [13 empty] | 0
2024-08-06 | 1146 | [13 empty] | 0
2024-08-07 | 1396 | [13 empty] | 0
2024-08-08 | 1594 | [13 empty] | 0
2024-08-09 | 1143 | [13 empty] | 0
2024-08-10 | 1395 | [13 empty] | 0
2024-08-11 | 1680 | [13 empty] | 117
2024-08-12 | 5555 | 0.527 | 1 | 6.9 | 10 | 14 | 4.6 | 2.95 | 0.44 | 16.51 | 10.59 | 3.59 | 1.56 | 50.25 | 95 | Craig Smith | 8:15am | 2024-08-22
2024-08-13 | 3664 | [13 empty] | 9
2024-08-14 | 3589 | [13 empty] | 15
2024-08-15 | 3137 | [13 empty] | 6
2024-08-16 | 2770 | [13 empty] | 6
2024-08-17 | 2616 | [13 empty] | 0
2024-08-18 | 2372 | [13 empty] | 0
2024-08-19 | 1915 | [13 empty] | 0
2024-08-20 | 2180 | [13 empty] | 0
2024-08-21 | 2051 | [13 empty] | 0
2024-08-22 | 1885 | [13 empty] | 0
2024-08-23 | 1843 | [13 empty] | 0
2024-08-24 | 1984 | [13 empty] | 0
2024-08-25 | 1375 | [13 empty] | 0
2024-08-26 | 1998 | 0.96 | 1 | 6.93 | 1 | 4 | 2.28 | 3.36 | 0.15 | 2.91 | 4.29 | 1.28 | 0.19 | 5.1 | 0 | Adriano Martinez | 10.50am | 2024-09-04
2024-08-27 | 1276 | [13 empty] | 0
2024-08-28 | 1687 | [13 empty] | 0
2024-08-29 | 1532 | [13 empty] | 0
2024-08-30 | 1433 | [13 empty] | 0
2024-08-31 | 1860 | [13 empty] | 0
2024-09-01 | 1440 | [13 empty] | 0
2024-09-02 | 1471 | [13 empty] | 0
2024-09-03 | 1279 | [13 empty] | 0
2024-09-04 | 1718 | [13 empty] | 0
2024-09-05 | 1300 | [13 empty] | 0
2024-09-06 | 1790 | [13 empty] | 0
2024-09-07 | 1410 | [13 empty] | 0
2024-09-08 | 1445 | [13 empty] | 0
2024-09-09 | 1388 | 0.81 | 1 | 7.5 | 20 | 5 | 1.4 | 4.31 | 0.2 | 2.14 | 5.98 | 1.39 | 0.28 | 6.94 | 5 | Adriano Martinez | 2.35pm | 2024-09-26
2024-09-10 | 1531 | [13 empty] | 0
2024-09-11 | 1347 | [13 empty] | 0
2024-09-12 | 1449 | [13 empty] | 0
2024-09-13 | 1269 | [13 empty] | 0
2024-09-14 | 1650 | [13 empty] | 0
2024-09-15 | 1243 | [13 empty] | 0
2024-09-16 | 1303 | [13 empty] | 0
2024-09-17 | 1486 | [13 empty] | 0
2024-09-18 | 1304 | [13 empty] | 0
2024-09-19 | 1490 | [13 empty] | 0
2024-09-20 | 1322 | [13 empty] | 0
2024-09-21 | 1693 | [13 empty] | 0
2024-09-22 | 1336 | [13 empty] | 0
2024-09-23 | 1304 | 0.75 | 1 | 7.31 | 655 | 5 | 1.6 | 3.97 | 0.27 | 1.83 | 4.55 | 1.15 | 0.31 | 5.73 | 0 | Adriano Martinez | 10:20am | 2024-10-23
2024-09-24 | 1146 | [13 empty] | 0
2024-09-25 | 1206 | [13 empty] | 0
2024-09-26 | 1594 | [13 empty] | 22
2024-09-27 | 2469 | [13 empty] | 0
2024-09-28 | 5229 | [13 empty] | 0
2024-09-29 | 3895 | [13 empty] | 0
2024-09-30 | 2951 | [13 empty] | 160
2024-10-01 | 2462 | [13 empty] | 17
2024-10-02 | 2466 | [13 empty] | 5
2024-10-03 | 2180 | [13 empty] | 6
2024-10-04 | 2411 | [13 empty] | 0
2024-10-05 | 2113 | [13 empty] | 0
2024-10-06 | 2113 | [13 empty] | 0
2024-10-07 | 1937 | 0.56 | 1 | 7.1 | 100 | 4 | 1.7 | 5.89 | 0.19 | 3.29 | 11.41 | 1.94 | 0.36 | 7.75 | 0 | Adriano Martinez | 8:40am | 2024-10-23
2024-10-08 | 1878 | [13 empty] | 0
2024-10-09 | 1930 | [13 empty] | 26
2024-10-10 | 1656 | [13 empty] | 0
2024-10-11 | 2530 | [13 empty] | 0
2024-10-12 | 1581 | [13 empty] | 0
2024-10-13 | 2205 | [13 empty] | 0
2024-10-14 | 1901 | [13 empty] | 11
2024-10-15 | 1826 | [13 empty] | 1
2024-10-16 | 1799 | [13 empty] | 3
2024-10-17 | 1354 | [13 empty] | 0
2024-10-18 | 1590 | [13 empty] | 0
2024-10-19 | 2055 | [13 empty] | 0
2024-10-20 | 1340 | [13 empty] | 3
2024-10-21 | 1521 | 0.67 | 3.78 | 6.92 | 10 | 4 | 1 | 3.95 | 0.16 | 1.52 | 6.01 | 5.75 | 0.25 | 6.08 | 0 | Craig Smith | 11:15am | 2024-11-12
2024-10-22 | 1772 | [13 empty] | 0
2024-10-23 | 1620 | [13 empty] | 0
2024-10-24 | 1597 | [13 empty] | 14
2024-10-25 | 1145 | [13 empty] | 0
2024-10-26 | 1472 | [13 empty] | 0
2024-10-27 | 1838 | [13 empty] | 5
2024-10-28 | 1380 | [13 empty] | 41
2024-10-29 | 1915 | [13 empty] | 0
2024-10-30 | 1344 | [13 empty] | 0
2024-10-31 | 1320 | [13 empty] | 0
2024-11-01 | 1871 | [13 empty] | 0
2024-11-02 | 1533 | [13 empty] | 0
2024-11-03 | 1388 | [13 empty] | 0
2024-11-04 | 1636 | 0.77 | 1 | 7.14 | 10 | 6 | 1.83 | 6 | 0.24 | 2.99 | 9.82 | 1.64 | 0.39 | 9.82 | 10 | Adriano Martinez | 8:50am | 2024-11-26
2024-11-05 | 1541 | [13 empty] | 0
2024-11-06 | 1541 | [13 empty] | 0
2024-11-07 | 1365 | [13 empty] | 0
2024-11-08 | 1394 | [13 empty] | 0
2024-11-09 | 1517 | [13 empty] | 0
2024-11-10 | 1452 | [13 empty] | 32
2024-11-11 | 1557 | [13 empty] | 55
2024-11-12 | 1894 | [13 empty] | 10
2024-11-13 | 2855 | [13 empty] | 8
2024-11-14 | 2778 | [13 empty] | 0
2024-11-15 | 2374 | [13 empty] | 0
2024-11-16 | 2031 | [13 empty] | 0
2024-11-17 | 1685 | [13 empty] | 0
2024-11-18 | 1989 | 0.37 | 1 | 7.09 | 10 | 2 | 1 | 7.18 | 0.17 | 1.69 | 12.1 | 1.69 | 0.29 | 3.37 | 12 | Craig Smith | 7:30am | 2024-12-19
2024-11-19 | 1889 | [13 empty] | 8
2024-11-20 | 1782 | [13 empty] | 1
2024-11-21 | 1731
2024-11-22 | 1944 | [13 empty] | 0
2024-11-23 | 1600 | [13 empty] | 0
2024-11-24 | 1844 | [13 empty] | 0
2024-11-25 | 1962 | [13 empty] | 3
2024-11-26 | 1613 | [13 empty] | 0
2024-11-27 | 1528 | [13 empty] | 0
2024-11-28 | 1700 | [13 empty] | 0
2024-11-29 | 1694 | [13 empty] | 0
2024-11-30 | 1477 | [13 empty] | 0
2024-12-01 | 1534 | [13 empty] | 40
2024-12-02 | 1920 | 0.48 | 1 | 7.04 | 10 | 2 | 1 | 4.45 | 0.19 | 0 | 6.83 | 1.53 | 0.29 | 3.07 | 0 | Craig Smith | 10:00am | 2024-12-20
2024-12-03 | 2004 | [13 empty] | 0
2024-12-04 | 1544 | [13 empty] | 0
2024-12-05 | 1615 | [13 empty] | 0
2024-12-06 | 1522 | [13 empty] | 0
2024-12-07 | 1759 | [13 empty] | 0
2024-12-08 | 1654 | [13 empty] | 0
2024-12-09 | 1315 | [13 empty] | 17
2024-12-10 | 1049 | [13 empty] | 8
2024-12-11 | 1875 | [13 empty] | 0
2024-12-12 | 1875 | [13 empty] | 0
2024-12-13 | 1797 | [13 empty] | 0
2024-12-14 | 1278 | [13 empty] | 0
2024-12-15 | 1757 | [13 empty] | 0
2024-12-16 | 1328 | 0.79 | 1 | 7.28 | 10 | 1 | 1.2 | 6.32 | 0.21 | 2.11 | 11.1 | 1.76 | 0.37 | 1.76 | 6 | Adriano Martinez | 9:30 | 2025-01-10
2024-12-17 | 1544 | [13 empty] | 0
2024-12-18 | 1060 | [13 empty] | 0
2024-12-19 | [14 empty] | 0
2024-12-20 | [14 empty] | 0
2024-12-21 | [14 empty] | 0
2024-12-22 | [14 empty] | 0
2024-12-23
2024-12-24
2024-12-25
2024-12-26
2024-12-27
2024-12-28
2024-12-29
2024-12-30
2024-12-31
2025-01-01
2025-01-02
2025-01-03
2025-01-04
2025-01-05
2025-01-06
2025-01-07
2025-01-08
2025-01-09
2025-01-10
2025-01-11
2025-01-12
2025-01-13
2025-01-14
2025-01-15
2025-01-16
2025-01-17
2025-01-18
2025-01-19
2025-01-20
2025-01-21
2025-01-22
2025-01-23
2025-01-24
2025-01-25
2025-01-26
2025-01-27
2025-01-28
2025-01-29
2025-01-30
2025-01-31
2025-02-01
2025-02-02
2025-02-03
2025-02-04
2025-02-05
2025-02-06
2025-02-07
2025-02-08
2025-02-09
2025-02-10
2025-02-11
2025-02-12
2025-02-13
2025-02-14
2025-02-15
2025-02-16
2025-02-17
2025-02-18
2025-02-19
2025-02-20
2025-02-21
2025-02-22
2025-02-23
2025-02-24
2025-02-25
2025-02-26
2025-02-27
2025-02-28
2025-03-01
2025-03-02
2025-03-03
2025-03-04
2025-03-05
2025-03-06
2025-03-07
2025-03-08
2025-03-09
2025-03-10
2025-03-11
2025-03-12
2025-03-13
2025-03-14
2025-03-15
2025-03-16
2025-03-17
2025-03-18
2025-03-19
2025-03-20
2025-03-21
2025-03-22
2025-03-23
2025-03-24
2025-03-25
2025-03-26
2025-03-27
2025-03-28
2025-03-29
2025-03-30
2025-03-31
2025-04-01
2025-04-02
2025-04-03
2025-04-04
2025-04-05
2025-04-06
2025-04-07
2025-04-08
2025-04-09
2025-04-10
2025-04-11
2025-04-12
2025-04-13
2025-04-14
2025-04-15
2025-04-16
2025-04-17
2025-04-18
2025-04-19
2025-04-20
2025-04-21
2025-04-22
2025-04-23
2025-04-24
2025-04-25
2025-04-26
2025-04-27
2025-04-28
2025-04-29
2025-04-30
2025-05-01
2025-05-02
2025-05-03
2025-05-04
2025-05-05
2025-05-06
2025-05-07
2025-05-08
2025-05-09
2025-05-10
2025-05-11
2025-05-12
2025-05-13
2025-05-14
2025-05-15
2025-05-16
2025-05-17
2025-05-18
2025-05-19
2025-05-20
2025-05-21
2025-05-22
2025-05-23
2025-05-24
2025-05-25
2025-05-26
2025-05-27
2025-05-28
2025-05-29
2025-05-30
2025-05-31
2025-06-01
2025-06-02
2025-06-03
2025-06-04
2025-06-05
2025-06-06
2025-06-07
2025-06-08
2025-06-09
2025-06-10
2025-06-11
2025-06-12
2025-06-13
2025-06-14
2025-06-15
2025-06-16
2025-06-17
2025-06-18
2025-06-19
2025-06-20
2025-06-21
2025-06-22
2025-06-23
2025-06-24
2025-06-25
2025-06-26
2025-06-27
2025-06-28
2025-06-29
2025-06-30