## Monitoring Point Locations
EPA Point 1 Discharge to water
EPA Point 3 Effluent quality monitoring
EPA Point 2 Total volume monitoring
EPA Point 4 Volume monitoring (Reuse)
EPA Point 6 Discharge to Golf Club irrigation
EPA Point 5 Effluent quality monitoring

## 12-13
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 12/13
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring |  |  |  | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | 1000 | -
2012-09-01 | 277.48 |  |  |  |  | 0 |  | 0
2012-09-02 | 317.782 |  |  |  |  | 0 |  | 0
2012-09-03 | 317.782 |  |  |  |  | 0 |  | 0
2012-09-04 | 272.459 |  |  |  |  | 0 |  | 0
2012-09-05 | 277.981 |  |  |  |  | 0 |  | 0
2012-09-06 | 279.097 |  |  |  |  | 0 |  | 0
2012-09-07 | 280.055 |  |  |  |  | 0 |  | 0
2012-09-08 | 197.314 |  |  |  |  | 0 |  | 0
2012-09-09 | 295.2515 |  |  |  |  | 0 |  | 0
2012-09-10 | 295.2515 | 2 | 6 | 2 | 5 | 0 |  | 0
2012-09-11 | 256.986 |  |  |  |  | 0 |  | 0
2012-09-12 | 273.812 |  |  |  |  | 0 |  | 0
2012-09-13 | 259.743 |  |  |  |  | 0 |  | 0
2012-09-14 | 292.427 |  |  |  |  | 0 |  | 0
2012-09-15 | 196.153 |  |  |  |  | 0 |  | 0
2012-09-16 | 288.9855 |  |  |  |  | 0 |  | 0
2012-09-17 | 288.9855 |  |  |  |  | 0 |  | 0
2012-09-18 | 324.344 |  |  |  |  | 0 |  | 26
2012-09-19 | 284.216 |  |  |  |  | 0 |  | 0
2012-09-20 | 260.291 |  |  |  |  | 0 |  | 0
2012-09-21 | 272.893 |  |  |  |  | 0 |  | 0
2012-09-22 | 229.433 |  |  |  |  | 0 |  | 5
2012-09-23 | 290.5615 |  |  |  |  | 0 |  | 0
2012-09-24 | 290.5615 |  |  |  |  | 0 |  | 0
2012-09-25 | 271.202 |  |  |  |  | 0 |  | 0
2012-09-26 | 248.674 |  |  |  |  | 0 |  | 0
2012-09-27 | 273.843 |  |  |  |  | 0 |  | 0
2012-09-28 | 265.377 |  |  |  |  | 0 |  | 0
2012-09-29 | 178.992 |  |  |  |  | 0 |  | 0
2012-09-30 | 260.271 |  |  |  |  | 0 |  | 0
2012-10-01 | 260.271 |  |  |  |  | 0 |  | 0
2012-10-02 | 296.185 |  |  |  |  | 0 |  | 0
2012-10-03 | 357.365 |  |  |  |  | 0 |  | 0
2012-10-04 | 269.406 |  |  |  |  | 0 |  | 0
2012-10-05 | 258.843 |  |  |  |  | 0 |  | 0
2012-10-06 | 193.838 |  |  |  |  | 0 |  | 0
2012-10-07 | 288.827 |  |  |  |  | 0 |  | 0
2012-10-08 | 288.827 | 2 | 26 | 2 | 24 | 0 |  | 0
2012-10-09 | 266.677 |  |  |  |  | 0 |  | 0
2012-10-10 | 245.516 |  |  |  |  | 0 |  | 0
2012-10-11 | 292.773 |  |  |  |  | 0 |  | 3
2012-10-12 | 269.473 |  |  |  |  | 215.45 |  | 0
2012-10-13 | 165.021 |  |  |  |  | 30.11 |  | 0
2012-10-14 | 319.8775 |  |  |  |  | 0 |  | 0
2012-10-15 | 319.8775 |  |  |  |  | 169.85 |  | 7
2012-10-16 | 282.033 |  |  |  |  | 264.43 |  | 0
2012-10-17 | 269.328 |  |  |  |  | 1031.23 |  | 0
2012-10-18 | 184.57 |  |  |  |  | 0 |  | 0
2012-10-19 | 277.987 |  |  |  |  | 0 |  | 0
2012-10-20 | 212.563 |  |  |  |  | 0 |  | 0
2012-10-21 | 286.4265 |  |  |  |  | 0 |  | 0
2012-10-22 | 286.4265 |  |  |  |  | 0 |  | 0
2012-10-23 | 247.242 |  |  |  |  | 0 |  | 0
2012-10-24 | 158.085 |  |  |  |  | 0 |  | 0
2012-10-25 | 329.853 |  |  |  |  | 0 |  | 0
2012-10-26 | 164.259 |  |  |  |  | 0 |  | 0
2012-10-27 | 264.4895 |  |  |  |  | 0 |  | 0
2012-10-28 | 264.4895 |  |  |  |  | 0 |  | 0
2012-10-29 | 264.233 |  |  |  |  | 0 |  | 0
2012-10-30 | 251.007 |  |  |  |  | 325.93 |  | 0
2012-10-31 | 223.765 |  |  |  |  | 350.31 |  | 0
2012-11-01 | 186.23 |  |  |  |  | 272.49 |  | 0
2012-11-02 | 339.979 |  |  |  |  | 0 |  | 0
2012-11-03 | 155.321 |  |  |  |  | 0 |  | 0
2012-11-04 | 297.0675 |  |  |  |  | 0 |  | 0
2012-11-05 | 297.0675 | 6 | 2 | 2 | 49 | 0 | 62 | 0
2012-11-06 | 271.667 |  |  |  |  | 123.84 |  | 0
2012-11-07 | 255.882 |  |  |  |  | 0 |  | 0
2012-11-08 | 144.536 |  |  |  |  | 248.95 |  | 0
2012-11-09 | 308.895 |  |  |  |  | 243.65 |  | 0
2012-11-10 | 256.918 |  |  |  |  | 0 |  | 0
2012-11-11 | 380.4145 |  |  |  |  | 0 |  | 0
2012-11-12 | 380.4145 |  |  |  |  | 0 |  | 76
2012-11-13 | 247.467 |  |  |  |  | 197.84 |  | 0
2012-11-14 | 257.765 |  |  |  |  | 123.62 |  | 0
2012-11-15 | 221.429 |  |  |  |  | 104.33 |  | 0
2012-11-16 | 276.71 |  |  |  |  | 215.02 |  | 0
2012-11-17 | 269.225 |  |  |  |  | 115.14 |  | 8
2012-11-18 | 213.6175 |  |  |  |  | 0 |  | 0
2012-11-19 | 213.6175 |  |  |  |  | 338.65 |  | 69
2012-11-20 | 321.159 |  |  |  |  | 315.96 |  | 0
2012-11-21 | 255.678 |  |  |  |  | 0 |  | 0
2012-11-22 | 314.851 |  |  |  |  | 0 |  | 0
2012-11-23 | 263.081 |  |  |  |  | 0 |  | 0
2012-11-24 | 238.486 |  |  |  |  | 0 |  | 0
2012-11-25 | 263.5035 |  |  |  |  | 0 |  | 0
2012-11-26 | 263.5035 |  |  |  |  | 0 |  | 0
2012-11-27 | 243.75 |  |  |  |  | 0 |  | 0
2012-11-28 | 222.462 |  |  |  |  | 0 |  | 0
2012-11-29 | 289.232 |  |  |  |  | 0 |  | 0
2012-11-30 | 191.44 |  |  |  |  | 94.78 |  | 0
2012-12-01 | 220.827 |  |  |  |  | 0 |  | 0
2012-12-02 | 262.907 |  |  |  |  | 0 |  | 0
2012-12-03 | 262.907 |  |  |  |  | 124.9 |  | 0
2012-12-04 | 275.558 | 10 | 24 | 2 | 84 | 0 | 500 | 16
2012-12-05 | 282.922 |  |  |  |  | 117.9 |  | 0
2012-12-06 | 256.757 |  |  |  |  | 0 |  | 0
2012-12-07 | 224.36 |  |  |  |  | 0 |  | 0
2012-12-08 | 182.55 |  |  |  |  | 0 |  | 0
2012-12-09 | 276.498 |  |  |  |  | 0 |  | 0
2012-12-10 | 276.498 |  |  |  |  | 294.33 |  | 8
2012-12-11 | 255.22 |  |  |  |  | 189.36 |  | 1
2012-12-12 | 176.462 |  |  |  |  | 0 |  | 0
2012-12-13 | 321.642 |  |  |  |  | 0 |  | 0
2012-12-14 | 227.172 |  |  |  |  | 0 |  | 2
2012-12-15 | 244.936 |  |  |  |  | 0 |  | 0
2012-12-16 | 254.972 |  |  |  |  | 0 |  | 0
2012-12-17 | 254.972 |  |  |  |  | 97.12 |  | 0
2012-12-18 | 257.012 |  |  |  |  | 296.45 |  | 0
2012-12-19 | 311.385 |  |  |  |  | 226.68 |  | 10
2012-12-20 | 296.038 |  |  |  |  | 0 |  | 12
2012-12-21 | 214.319 |  |  |  |  | 0 |  | 0
2012-12-22 | 381.888 |  |  |  |  | 0 |  | 28
2012-12-23 | 278.357 |  |  |  |  | 0 |  | 0
2012-12-24 | 278.357 |  |  |  |  | 0 |  | 6
2012-12-25 | 249.664 |  |  |  |  | 0 |  | 0
2012-12-26 | 249.664 |  |  |  |  | 0 |  | 10
2012-12-27 | 287.361 |  |  |  |  | 0 |  | 0
2012-12-28 | 236.782 |  |  |  |  | 0 |  | 0
2012-12-29 | 267.578 |  |  |  |  | 0 |  | 2
2012-12-30 | 263.777 |  |  |  |  | 0 |  | 0
2012-12-31 | 263.777 |  |  |  |  | 0 |  | 0
2013-01-01 | 219.8865 |  |  |  |  | 0 |  | 0
2013-01-02 | 219.8865 |  |  |  |  | 0 |  | 0
2013-01-03 | 290.331 |  |  |  |  | 0 |  | 0
2013-01-04 | 208.159 | 17 | 2 | 2 | 90 | 0 | 48 | 0
2013-01-05 | 178 |  |  |  |  | 0 |  | 0
2013-01-06 | 239.14 |  |  |  |  | 0 |  | 0
2013-01-07 | 239.14 |  |  |  |  | 0 |  | 2
2013-01-08 | 239.03 |  |  |  |  | 0 |  | 0
2013-01-09 | 136.993 |  |  |  |  | 0 |  | 0
2013-01-10 | 286.719 |  |  |  |  | 0 |  | 0
2013-01-11 | 209.158 |  |  |  |  | 174 |  | 0
2013-01-12 | 172.563 |  |  |  |  | 0 |  | 0
2013-01-13 | 228.102 |  |  |  |  | 0 |  | 0
2013-01-14 | 228.102 |  |  |  |  | 171 |  | 0
2013-01-15 | 257.66 |  |  |  |  | 213 |  | 7
2013-01-16 | 225.097 |  |  |  |  | 87 |  | 0
2013-01-17 | 217.483 |  |  |  |  | 0 |  | 0
2013-01-18 | 211.594 |  |  |  |  | 0 |  | 0
2013-01-19 | 175.319 |  |  |  |  | 0 |  | 0
2013-01-20 | 247.55 |  |  |  |  | 0 |  | 0
2013-01-21 | 247.55 |  |  |  |  | 0 |  | 8
2013-01-22 | 223.95 |  |  |  |  | 0 |  | 0
2013-01-23 | 194.03 |  |  |  |  | 308 |  | 0
2013-01-24 | 262.032 |  |  |  |  | 0 |  | 2
2013-01-25 | 244.867 |  |  |  |  | 0 |  | 8
2013-01-26 | 198.726 |  |  |  |  | 0 |  | 7
2013-01-27 | 1292.268 |  |  |  |  | 0 |  | 0
2013-01-28 | 1292.268 |  |  |  |  | 0 |  | 154
2013-01-29 | 1902.23 |  |  |  |  | 0 |  | 24
2013-01-30 | 880.754 |  |  |  |  | 0 |  | 0
2013-01-31 | 765.717 | 7 | 2 | 2 | 35 | 0 | 2 | 0
2013-02-01 | 442.946 |  |  |  |  | 0 |  | 0
2013-02-02 | 286.767 |  |  |  |  | 0 |  | 5
2013-02-03 | 370.286 |  |  |  |  | 0 |  | 0
2013-02-04 | 370.286 |  |  |  |  | 0 |  | 0
2013-02-05 | 268.116 |  |  |  |  | 0 |  | 2
2013-02-06 | 341.41 |  |  |  |  | 0 |  | 6
2013-02-07 | 354.894 |  |  |  |  | 0 |  | 16
2013-02-08 | 304.762 |  |  |  |  | 0 |  | 0
2013-02-09 | 263.972 |  |  |  |  | 0 |  | 4
2013-02-10 | 341.9195 |  |  |  |  | 0 |  | 0
2013-02-11 | 341.9195 |  |  |  |  | 0 |  | 1
2013-02-12 | 289.077 |  |  |  |  | 0 |  | 0
2013-02-13 | 318.035 |  |  |  |  | 0 |  | 13
2013-02-14 | 284.259 |  |  |  |  | 0 |  | 4
2013-02-15 | 401.455 |  |  |  |  | 0 |  | 15
2013-02-16 | 273.236 |  |  |  |  | 0 |  | 0
2013-02-17 | 411.9715 |  |  |  |  | 0 |  | 0
2013-02-18 | 411.9715 |  |  |  |  | 0 |  | 8
2013-02-19 | 1925.999 |  |  |  |  | 0 |  | 67
2013-02-20 | 1904.691 |  |  |  |  | 0 |  | 23
2013-02-21 | 1524.162 |  |  |  |  | 0 |  | 13
2013-02-22 | 1488.149 |  |  |  |  | 0 |  | 35
2013-02-23 | 2204.741 |  |  |  |  | 0 |  | 64
2013-02-24 | 1692.3195 |  |  |  |  | 0 |  | 0
2013-02-25 | 1692.3195 | 2 | 180 | 2 | 6 | 0 | 2 | 26
2013-02-26 | 1997.961 |  |  |  |  | 0 |  | 20
2013-02-27 | 2062.493 |  |  |  |  | 0 |  | 9
2013-02-28 | 1335.917 |  |  |  |  | 0 |  | 2
2013-03-01 | 742.812 |  |  |  |  | 0 |  | 0
2013-03-02 | 1224 |  |  |  |  | 0 |  | 25
2013-03-03 | 2121.581 |  |  |  |  | 0 |  | 0
2013-03-04 | 2121.58 |  |  |  |  | 0 |  | 75
2013-03-05 | 1732.413 |  |  |  |  | 0 |  | 6
2013-03-06 | 939.71 |  |  |  |  | 0 |  | 0
2013-03-07 | 721.366 |  |  |  |  | 0 |  | 5
2013-03-08 | 711.448 |  |  |  |  | 0 |  | 0
2013-03-09 | 521.547 |  |  |  |  | 0 |  | 0
2013-03-10 | 668.837 |  |  |  |  | 0 |  | 0
2013-03-11 | 668.837 |  |  |  |  | 0 |  | 9
2013-03-12 | 434.792 |  |  |  |  | 0 |  | 0
2013-03-13 | 650.952 |  |  |  |  | 0 |  | 0
2013-03-14 | 402.224 |  |  |  |  | 0 |  | 4
2013-03-15 | 424.84 |  |  |  |  | 0 |  | 0
2013-03-16 | 380.058 |  |  |  |  | 0 |  | 0
2013-03-17 | 430.799 |  |  |  |  | 0 |  | 0
2013-03-18 | 430.799 |  |  |  |  | 0 |  | 0
2013-03-19 | 254.704 |  |  |  |  | 0 |  | 2.5
2013-03-20 | 432.2 |  |  |  |  | 0 |  | 0
2013-03-21 | 426.562 |  |  |  |  | 0 |  | 3
2013-03-22 | 352.983 |  |  |  |  | 0 |  | 0
2013-03-23 | 270.059 |  |  |  |  | 0 |  | 0
2013-03-24 | 385.8295 |  |  |  |  | 0 |  | 0
2013-03-25 | 385.8295 | 4 | 14 | 2 | 21 | 0 | 40 | 0
2013-03-26 | 393.494 |  |  |  |  | 0 |  | 0
2013-03-27 | 314.988 |  |  |  |  | 0 |  | 0
2013-03-28 | 350.606 |  |  |  |  | 0 |  | 0
2013-03-29 | 256.801 |  |  |  |  | 0 |  | 0
2013-03-30 | 424.094 |  |  |  |  | 0 |  | 4
2013-03-31 | 450.059 |  |  |  |  | 0 |  | 0
2013-04-01 | 450.059 |  |  |  |  | 0 |  | 0
2013-04-02 | 513.788 |  |  |  |  | 0 |  | 29
2013-04-03 | 371.769 |  |  |  |  | 0 |  | 0
2013-04-04 | 751.652 |  |  |  |  | 0 |  | 22
2013-04-05 | 1806.107 |  |  |  |  | 0 |  | 40
2013-04-06 | 1288.753 |  |  |  |  | 0 |  | 18
2013-04-07 | 1387.4965 |  |  |  |  | 0 |  | 0
2013-04-08 | 1387.4965 |  |  |  |  | 0 |  | 33
2013-04-09 | 753.655 |  |  |  |  | 0 |  | 7
2013-04-10 | 924.676 |  |  |  |  | 0 |  | 23
2013-04-11 | 701.999 |  |  |  |  | 0 |  | 0
2013-04-12 | 727.758 |  |  |  |  | 0 |  | 2
2013-04-13 | 1542.28 |  |  |  |  | 0 |  | 32
2013-04-14 | 1634.16 |  |  |  |  | 0 |  | 0
2013-04-15 | 1634.16 |  |  |  |  | 0 |  | 13
2013-04-16 | 888.619 |  |  |  |  | 0 |  | 0
2013-04-17 | 956.99 |  |  |  |  | 0 |  | 13
2013-04-18 | 895.325 |  |  |  |  | 0 |  | 0
2013-04-19 | 688.21 |  |  |  |  | 0 |  | 0
2013-04-20 | 445.551 |  |  |  |  | 0 |  | 0
2013-04-21 | 513.709 |  |  |  |  | 0 |  | 0
2013-04-22 | 513.709 | 2 | 28 | 2 | 10 | 0 | 50 | 0
2013-04-23 | 467.622 |  |  |  |  | 0 |  | 0
2013-04-24 | 391.3 |  |  |  |  | 0 |  | 0
2013-04-25 | 281.417 |  |  |  |  | 0 |  | 0
2013-04-26 | 500.723 |  |  |  |  | 0 |  | 0
2013-04-27 | 271.651 |  |  |  |  | 0 |  | 0
2013-04-28 | 383.8555 |  |  |  |  | 0 |  | 0
2013-04-29 | 383.8555 |  |  |  |  | 0 |  | 0
2013-04-30 | 321.62 |  |  |  |  | 0 |  | 0
2013-05-01 | 369.934 |  |  |  |  | 0 |  | 0
2013-05-02 | 402.394 |  |  |  |  | 0 |  | 0
2013-05-03 | 254.787 |  |  |  |  | 0 |  | 0
2013-05-04 | 288.056 |  |  |  |  | 0 |  | 0
2013-05-05 | 339.1795 |  |  |  |  | 0 |  | 0
2013-05-06 | 339.1795 |  |  |  |  | 70 |  | 0
2013-05-07 | 339.147 |  |  |  |  | 0 |  | 9
2013-05-08 | 378.664 |  |  |  |  | 0 |  | 0
2013-05-09 | 302.246 |  |  |  |  | 0 |  | 0
2013-05-10 | 357.962 |  |  |  |  | 0 |  | 2
2013-05-11 | 673.576 |  |  |  |  | 0 |  | 30
2013-05-12 | 665.8565 |  |  |  |  | 0 |  | 0
2013-05-13 | 665.8565 |  |  |  |  | 0 |  | 9
2013-05-14 | 447.449 |  |  |  |  | 0 |  | 4
2013-05-15 | 478.853 |  |  |  |  | 0 |  | 0
2013-05-16 | 441.414 |  |  |  |  | 0 |  | 0
2013-05-17 | 346.058 |  |  |  |  | 0 |  | 0
2013-05-18 | 265.137 |  |  |  |  | 0 |  | 0
2013-05-19 | 384.6695 |  |  |  |  | 0 |  | 0
2013-05-20 | 384.6695 | 7 | 28 | 2 | 26 | 97 | 18 | 0
2013-05-21 | 337.406 |  |  |  |  | 0 |  | 0
2013-05-22 | 315.661 |  |  |  |  | 0 |  | 0
2013-05-23 | 367.48 |  |  |  |  | 0 |  | 3
2013-05-24 | 325.393 |  |  |  |  | 0 |  | 0
2013-05-25 | 502.007 |  |  |  |  | 0 |  | 23
2013-05-26 | 420.2 |  |  |  |  | 0 |  | 0
2013-05-27 | 420.2 |  |  |  |  | 0 |  | 0
2013-05-28 | 382.21 |  |  |  |  | 0 |  | 0
2013-05-29 | 379.787 |  |  |  |  | 0 |  | 0
2013-05-30 | 425.733 |  |  |  |  | 0 |  | 1
2013-05-31 | 278.694 |  |  |  |  | 0 |  | 0
2013-06-01 | 341.7 |  |  |  |  | 0 |  | 0
2013-06-02 | 371.191 |  |  |  |  | 0 |  | 0
2013-06-03 | 371.191 |  |  |  |  | 0 |  | 0
2013-06-04 | 264 |  |  |  |  | 0 |  | 0
2013-06-05 | 526.313 |  |  |  |  | 0 |  | 0
2013-06-06 | 225.596 |  |  |  |  | 0 |  | 0
2013-06-07 | 275.043 |  |  |  |  | 0 |  | 0
2013-06-08 | 264.965 |  |  |  |  | 0 |  | 2
2013-06-09 | 390.6325 |  |  |  |  | 0 |  | 0
2013-06-10 | 390.6325 |  |  |  |  | 0 |  | 10
2013-06-11 | 478.026 |  |  |  |  | 0 |  | 0
2013-06-12 | 317.556 |  |  |  |  | 0 |  | 8
2013-06-13 | 1087.756 |  |  |  |  | 0 |  | 33
2013-06-14 | 588.686 |  |  |  |  | 0 |  | 0
2013-06-15 | 377.435 |  |  |  |  | 0 |  | 0
2013-06-16 | 430.2345 |  |  |  |  | 0 |  | 0
2013-06-17 | 430.2345 | 2 | 20 | 2 | 5 | 0 | 11 | 0
2013-06-18 | 392.097 |  |  |  |  | 0 |  | 0
2013-06-19 | 317.553 |  |  |  |  | 0 |  | 0
2013-06-20 | 288.143 |  |  |  |  | 0 |  | 0
2013-06-21 | 398.874 |  |  |  |  | 0 |  | 6
2013-06-22 | 257.346 |  |  |  |  | 0 |  | 0
2013-06-23 | 393.105 |  |  |  |  | 0 |  | 0
2013-06-24 | 393.105 |  |  |  |  | 0 |  | 0
2013-06-25 | 333.052 |  |  |  |  | 0 |  | 0
2013-06-26 | 247.378 |  |  |  |  | 0 |  | 1
2013-06-27 | 264.227 |  |  |  |  | 0 |  | 0
2013-06-28 | 264.227 |  |  |  |  | 0 |  | 12
2013-06-29 | 656.457 |  |  |  |  | 0 |  | 0
2013-06-30 | 656.457 |  |  |  |  | 0 |  | 22
2013-07-01 | 1071.603 |  |  |  |  | 0 |  | 28
2013-07-02 | 2296.9 |  |  |  |  | 0 |  | 43
2013-07-03 | 1191.515 |  |  |  |  | 0 |  | 1
2013-07-04 | 549.619 |  |  |  |  | 0 |  | 0
2013-07-05 | 850.6 |  |  |  |  | 0 |  | 0
2013-07-06 | 446.886 |  |  |  |  | 0 |  | 0
2013-07-07 | 520.6095 |  |  |  |  | 0 |  | 0
2013-07-08 | 520.6095 |  |  |  |  | 0 |  | 0
2013-07-09 | 353.893 |  |  |  |  | 0 |  | 0
2013-07-10 | 465.113 |  |  |  |  | 0 |  | 6
2013-07-11 | 446.418 |  |  |  |  | 0 |  | 0
2013-07-12 | 465.793 |  |  |  |  | 0 |  | 0
2013-07-13 | 502.758 |  |  |  |  | 0 |  | 0
2013-07-14 | 440.56 |  |  |  |  | 0 |  | 0
2013-07-15 | 440.56 | 2 | 4 | 2 | 5 | 0 | 14 | 0
2013-07-16 | 428.085 |  |  |  |  | 0 |  | 0
2013-07-17 | 365.794 |  |  |  |  | 0 |  | 0
2013-07-18 | 311.468 |  |  |  |  | 0 |  | 3
2013-07-19 | 459.952 |  |  |  |  | 0 |  | 0
2013-07-20 | 309 |  |  |  |  | 0 |  | 0
2013-07-21 | 532.4385 |  |  |  |  | 0 |  | 0
2013-07-22 | 532.4385 |  |  |  |  | 0 |  | 6
2013-07-23 | 426.98 |  |  |  |  | 0 |  | 0
2013-07-24 | 362.02 |  |  |  |  | 0 |  | 0
2013-07-25 | 319.002 |  |  |  |  | 0 |  | 0
2013-07-26 | 416.122 |  |  |  |  | 0 |  | 0
2013-07-27 | 231.499 |  |  |  |  | 0 |  | 0
2013-07-28 | 363.5125 |  |  |  |  | 0 |  | 0
2013-07-29 | 363.5125 |  |  |  |  | 0 |  | 0
2013-07-30 | 344.018 |  |  |  |  | 0 |  | 0
2013-07-31 | 245.011 |  |  |  |  | 0 |  | 0
2013-08-01 | 422.438 |  |  |  |  | 0 |  | 0
2013-08-02 | 311.738 |  |  |  |  | 0 |  | 0
2013-08-03 | 298.149 |  |  |  |  | 0 |  | 0
2013-08-04 | 318.43 |  |  |  |  | 0 |  | 0
2013-08-05 | 318.43 |  |  |  |  | 0 |  | 0
2013-08-06 | 360.648 |  |  |  |  | 0 |  | 0
2013-08-07 | 315.476 |  |  |  |  | 0 |  | 0
2013-08-08 | 298.38 |  |  |  |  | 0 |  | 0
2013-08-09 | 302.471 |  |  |  |  | 0 |  | 0
2013-08-10 | 194.644 |  |  |  |  | 0 |  | 0
2013-08-11 | 653.926 |  |  |  |  | 0 |  | 0
2013-08-12 | 653.926 | 5 | 16 | 2 | 10 | 0 | 54 | 0
2013-08-13 | 316.56 |  |  |  |  | 0 |  | 0
2013-08-14 | 278.73 |  |  |  |  | 0 |  | 0
2013-08-15 | 367.197 |  |  |  |  | 0 |  | 12
2013-08-16 | 272.675 |  |  |  |  | 0 |  | 0
2013-08-17 | 238.155 |  |  |  |  | 0 |  | 0
2013-08-18 | 334.1315 |  |  |  |  | 0 |  | 0
2013-08-19 | 334.1315 |  |  |  |  | 0 |  | 0
2013-08-20 | 261.718 |  |  |  |  | 0 |  | 0
2013-08-21 | 271.398 |  |  |  |  | 0 |  | 0
2013-08-22 | 279.852 |  |  |  |  | 0 |  | 0
2013-08-23 | 232.052 |  |  |  |  | 0 |  | 0
2013-08-24 | 258.378 |  |  |  |  | 0 |  | 0
2013-08-25 | 303.5975 |  |  |  |  | 0 |  | 0
2013-08-26 | 303.5975 |  |  |  |  | 0 |  | 0
2013-08-27 | 305.666 |  |  |  |  | 0 |  | 0
2013-08-28 | 264.198 |  |  |  |  | 0 |  | 0
2013-08-29 | 221.155 |  |  |  |  | 0 |  | 0
2013-08-30 | 263.184 |  |  |  |  | 0 |  | 0
2013-08-31 | 225.618 |  |  |  |  | 0 |  | 0
MINIMUM | 136.993 | 2 | 2 | 2 | 5 | 0 | 2 | 0
AVERAGE | 444.8968 | 5.2308 | 27.0769 | 2 | 28.4615 | 37.5985 | 72.8182 | 4.037
MAXIMUM | 2296.9 | 17 | 180 | 2 | 90 | 325.93 | 500 | 154
| 162387.348 |  |  |  |  | 7248.32 |  | 1473.5
| SAMPLE COUNT | 13

## 13-14
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 13/14
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring |  |  |  | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | 1000 | -
2013-09-01 | 330.59 |  |  |  |  | 0 |  | 0
2013-09-02 | 250 |  |  |  |  | 0 |  | 0
2013-09-03 | 261.501 |  |  |  |  | 165 |  | 0
2013-09-04 | 287.19 |  |  |  |  | 50 |  | 0
2013-09-05 | 263.377 |  |  |  |  | 44 |  | 0
2013-09-06 | 280.127 |  |  |  |  | 284 |  | 0
2013-09-07 | 193.953 |  |  |  |  | 0 |  | 0
2013-09-08 | 284.171 |  |  |  |  | 0 |  | 0
2013-09-09 | 284.171 | 3 | 2 | 2 | 33 | 57 | 2 | 0
2013-09-10 | 291.757 |  |  |  |  | 163 |  | 0
2013-09-11 | 261.422 |  |  |  |  | 73 |  | 0
2013-09-12 | 249.219 |  |  |  |  | 58 |  | 0
2013-09-13 | 252.693 |  |  |  |  | 39 |  | 0
2013-09-14 | 202.18 |  |  |  |  | 0 |  | 0
2013-09-15 | 265.7055 |  |  |  |  | 0 |  | 0
2013-09-16 | 265.7055 |  |  |  |  | 58 |  | 0
2013-09-17 | 566.501 |  |  |  |  | 126 |  | 57
2013-09-18 | 304.577 |  |  |  |  | 75 |  | 0
2013-09-19 | 275.961 |  |  |  |  | 0 |  | 0
2013-09-20 | 306.674 |  |  |  |  | 0 |  | 0
2013-09-21 | 249.942 |  |  |  |  | 0 |  | 0
2013-09-22 | 274.2605 |  |  |  |  | 0 |  | 0
2013-09-23 | 274.2605 |  |  |  |  | 84 |  | 0
2013-09-24 | 245.609 |  |  |  |  | 0 |  | 0
2013-09-25 | 251.181 |  |  |  |  | 80 |  | 0
2013-09-26 | 255.067 |  |  |  |  | 91 |  | 0
2013-09-27 | 255.047 |  |  |  |  | 0 |  | 0
2013-09-28 | 333.747 |  |  |  |  | 0 |  | 0
2013-09-29 | 333.747 |  |  |  |  | 0 |  | 0
2013-09-30 | 333.747 |  |  |  |  | 0 |  | 0
2013-10-01 | 255 |  |  |  |  | 77 |  | 0
2013-10-02 | 274.803 |  |  |  |  | 51 |  | 0
2013-10-03 | 204.4365 |  |  |  |  | 0 |  | 0
2013-10-04 | 180 |  |  |  |  | 71 |  | 0
2013-10-05 | 149.682 |  |  |  |  | 0 |  | 0
2013-10-06 | 301.5495 |  |  |  |  | 0 |  | 0
2013-10-07 | 301.5495 |  |  |  |  | 0 |  | 0
2013-10-08 | 256.843 | 8 | 2 | 2 | 50 | 0 | 2 | 0
2013-10-09 | 256.843 |  |  |  |  | 75 |  | 0
2013-10-10 | 234.017 |  |  |  |  | 105 |  | 0
2013-10-11 | 236.813 |  |  |  |  | 0 |  | 0
2013-10-12 | 305.914 |  |  |  |  | 0 |  | 0
2013-10-13 | 305.914 |  |  |  |  | 0 |  | 0
2013-10-14 | 305.914 |  |  |  |  | 0 |  | 0
2013-10-15 | 235 |  |  |  |  | 0 |  | 0
2013-10-16 | 236.233 |  |  |  |  | 0 |  | 0
2013-10-17 | 236.233 |  |  |  |  | 0 |  | 0
2013-10-18 | 208 |  |  |  |  | 0 |  | 0
2013-10-19 | 249.6787 |  |  |  |  | 0 |  | 0
2013-10-20 | 249.6787 |  |  |  |  | 0 |  | 0
2013-10-21 | 249.6787 |  |  |  |  | 54 |  | 0
2013-10-22 | 222.329 |  |  |  |  | 55 |  | 0
2013-10-23 | 238.453 |  |  |  |  | 68 |  | 0
2013-10-24 | 235.8805 |  |  |  |  | 0 |  | 0
2013-10-25 | 260 |  |  |  |  | 60 |  | 0
2013-10-26 | 317.6363 |  |  |  |  | 0 |  | 0
2013-10-27 | 317.6363 |  |  |  |  | 0 |  | 0
2013-10-28 | 317.6363 |  |  |  |  | 0 |  | 0
2013-10-29 | 219 |  |  |  |  | 91 |  | 0
2013-10-30 | 198.638 |  |  |  |  | 0 |  | 5
2013-10-31 | 252.796 |  |  |  |  | 77 |  | 0
2013-11-01 | 224.806 |  |  |  |  | 78 |  | 0
2013-11-02 | 201.09 |  |  |  |  | 0 |  | 0
2013-11-03 | 252.8295 |  |  |  |  | 0 |  | 0
2013-11-04 | 252.8295 | 18 | 8 | 2 | 100 | 328 | 2 | 0
2013-11-05 | 218.109 |  |  |  |  | 284 |  | 0
2013-11-06 | 252.208 |  |  |  |  | 328 |  | 0
2013-11-07 | 211.626 |  |  |  |  | 0 |  | 0
2013-11-08 | 196.338 |  |  |  |  | 0 |  | 0
2013-11-09 | 242.586 |  |  |  |  | 0 |  | 0
2013-11-10 | 275.212 |  |  |  |  | 0 |  | 0
2013-11-11 | 275.212 |  |  |  |  | 0 |  | 7
2013-11-12 | 282.919 |  |  |  |  | 0 |  | 10
2013-11-13 | 225.09 |  |  |  |  | 71 |  | 0
2013-11-14 | 565.919 |  |  |  |  | 92 |  | 48
2013-11-15 | 425.642 |  |  |  |  | 106 |  | 18
2013-11-16 | 202.005 |  |  |  |  | 0 |  | 0
2013-11-17 | 299.521 |  |  |  |  | 0 |  | 0
2013-11-18 | 299.521 |  |  |  |  | 0 |  | 0
2013-11-19 | 236.137 |  |  |  |  | 137 |  | 0
2013-11-20 | 256.878 |  |  |  |  | 0 |  | 0
2013-11-21 | 225.026 |  |  |  |  | 91 |  | 0
2013-11-22 | 239.604 |  |  |  |  | 71 |  | 0
2013-11-23 | 243.263 |  |  |  |  | 0 |  | 16
2013-11-24 | 540.2445 |  |  |  |  | 0 |  | 0
2013-11-25 | 540.2445 |  |  |  |  | 0 |  | 42
2013-11-26 | 257.314 |  |  |  |  | 75 |  | 0
2013-11-27 | 292.671 |  |  |  |  | 0 |  | 0
2013-11-28 | 212.929 |  |  |  |  | 99 |  | 0
2013-11-29 | 246.354 |  |  |  |  | 59 |  | 0
2013-11-30 | 411.665 |  |  |  |  | 0 |  | 0
2013-12-01 | 539.236 |  |  |  |  | 0 |  | 0
2013-12-02 | 539.236 | 7 | 160 | 2 | 49 | 52 | 2 | 9
2013-12-03 | 319.696 |  |  |  |  | 58 |  | 0
2013-12-04 | 217.06 |  |  |  |  | 0 |  | 0
2013-12-05 | 285.377 |  |  |  |  | 121 |  | 0
2013-12-06 | 269.602 |  |  |  |  | 0 |  | 0
2013-12-07 | 225.479 |  |  |  |  | 0 |  | 0
2013-12-08 | 243.1145 |  |  |  |  | 0 |  | 0
2013-12-09 | 243.1145 |  |  |  |  | 0 |  | 0
2013-12-10 | 277.607 |  |  |  |  | 54 |  | 0
2013-12-11 | 242 |  |  |  |  | 0 |  | 0
2013-12-12 | 307.029 |  |  |  |  | 0 |  | 0
2013-12-13 | 269 |  |  |  |  | 0 |  | 0
2013-12-14 | 237.958 |  |  |  |  | 0 |  | 0
2013-12-15 | 271.233 |  |  |  |  | 0 |  | 0
2013-12-16 | 271.233 |  |  |  |  | 283 |  | 0
2013-12-17 | 261.212 |  |  |  |  | 185 |  | 0
2013-12-18 | 267.437 |  |  |  |  | 107 |  | 0
2013-12-19 | 236.766 |  |  |  |  | 0 |  | 0
2013-12-20 | 225.784 |  |  |  |  | 0 |  | 0
2013-12-21 | 224.761 |  |  |  |  | 0 |  | 0
2013-12-22 | 240.492 |  |  |  |  | 0 |  | 0
2013-12-23 | 240.492 |  |  |  |  | 0 |  | 0
2013-12-24 | 281.973 |  |  |  |  | 108 |  | 0
2013-12-25 | 207.5495 |  |  |  |  | 0 |  | 0
2013-12-26 | 207.5495 |  |  |  |  | 0 |  | 0
2013-12-27 | 323.167 |  |  |  |  | 0 |  | 0
2013-12-28 | 190.582 |  |  |  |  | 0 |  | 0
2013-12-29 | 204.906 |  |  |  |  | 0 |  | 0
2013-12-30 | 311.64 |  |  |  |  | 0 |  | 0
2013-12-31 | 167.924 | 3 | 240 | 2 | 26 | 0 | 2 | 0
2014-01-01 | 236.253 |  |  |  |  | 0 |  | 0
2014-01-02 | 265.657 |  |  |  |  | 0 |  | 0
2014-01-03 | 227.841 |  |  |  |  | 0 |  | 0
2014-01-04 | 166.568 |  |  |  |  | 0 |  | 0
2014-01-05 | 213.4925 |  |  |  |  | 0 |  | 0
2014-01-06 | 213.4925 |  |  |  |  | 0 |  | 0
2014-01-07 | 262.321 |  |  |  |  | 77 |  | 0
2014-01-08 | 232.347 |  |  |  |  | 105 |  | 8
2014-01-09 | 255.583 |  |  |  |  | 0 |  | 5
2014-01-10 | 195.08 |  |  |  |  | 0 |  | 2
2014-01-11 | 168.47 |  |  |  |  | 0 |  | 0
2014-01-12 | 227.2105 |  |  |  |  | 0 |  | 0
2014-01-13 | 227.2105 |  |  |  |  | 0 |  | 1
2014-01-14 | 234.174 |  |  |  |  | 0 |  | 15
2014-01-15 | 221.664 |  |  |  |  | 0 |  | 1
2014-01-16 | 215.041 |  |  |  |  | 122 |  | 0
2014-01-17 | 203.979 |  |  |  |  | 67 |  | 0
2014-01-18 | 197.316 |  |  |  |  | 0 |  | 0
2014-01-19 | 237.1055 |  |  |  |  | 0 |  | 0
2014-01-20 | 237.1055 |  |  |  |  | 0 |  | 0
2014-01-21 | 177 | 10 | 148 | 2 | 75 | 0 | 2 | 0
2014-01-22 | 177.12 |  |  |  |  | 930 |  | 0
2014-01-23 | 261.679 |  |  |  |  | 0 |  | 18
2014-01-24 | 283.388 |  |  |  |  | 0 |  | 19
2014-01-25 | 235.776 |  |  |  |  | 0 |  | 11
2014-01-26 | 270.766 |  |  |  |  | 0 |  | 0
2014-01-27 | 270.766 |  |  |  |  | 64 |  | 2
2014-01-28 | 272.751 |  |  |  |  | 0 |  | 0
2014-01-29 | 249.531 |  |  |  |  | 0 |  | 0
2014-01-30 | 215.577 |  |  |  |  | 48 |  | 0
2014-01-31 | 198.11 |  |  |  |  | 72 |  | 0
2014-02-01 | 176.476 |  |  |  |  | 0 |  | 0
2014-02-02 | 236.5065 |  |  |  |  | 0 |  | 0
2014-02-03 | 236.5065 |  |  |  |  | 98 |  | 1
2014-02-04 | 250.188 |  |  |  |  | 68 |  | 0
2014-02-05 | 195.672 |  |  |  |  | 83 |  | 3
2014-02-06 | 246.69 |  |  |  |  | 165 |  | 8
2014-02-07 | 191.002 |  |  |  |  | 87 |  | 4
2014-02-08 | 209.915 |  |  |  |  | 0 |  | 0
2014-02-09 | 232.648 |  |  |  |  | 0 |  | 0
2014-02-10 | 232.648 |  |  |  |  | 191 |  | 0
2014-02-11 | 219.161 |  |  |  |  | 88 |  | 0
2014-02-12 | 216.277 |  |  |  |  | 137 |  | 0
2014-02-13 | 199.101 |  |  |  |  | 122 |  | 0
2014-02-14 | 196.325 |  |  |  |  | 0 |  | 0
2014-02-15 | 193.09 |  |  |  |  | 0 |  | 0
2014-02-16 | 224.1205 |  |  |  |  | 0 |  | 0
2014-02-17 | 448 |  |  |  |  | 0 |  | 0
2014-02-18 | 197.977 |  |  |  |  | 0 |  | 0
2014-02-19 | 178.986 |  |  |  |  | 144 |  | 0
2014-02-20 | 200.438 |  |  |  |  | 185 |  | 0
2014-02-21 | 245.921 |  |  |  |  | 272 |  | 0
2014-02-22 | 176.583 |  |  |  |  | 0 |  | 0
2014-02-23 | 218.383 |  |  |  |  | 0 |  | 0
2014-02-24 | 436 |  |  |  |  | 0 |  | 0
2014-02-25 | 186 | 18 | 74 | 2 | 93 | 0 | 2 | 8
2014-02-26 | 206.05 |  |  |  |  | 0 |  | 0
2014-02-27 | 212.282 |  |  |  |  | 0 |  | 0
2014-02-28 | 241.686 |  |  |  |  | 0 |  | 0
2014-03-01 | 195.346 |  |  |  |  | 0 |  | 2
2014-03-02 | 229.8255 |  |  |  |  | 0 |  | 0
2014-03-03 | 459 |  |  |  |  | 0 |  | 11
2014-03-04 | 198.445 |  |  |  |  | 128 |  | 0
2014-03-05 | 207.58 |  |  |  |  | 109 |  | 0
2014-03-06 | 210.384 |  |  |  |  | 95 |  | 0
2014-03-07 | 219.862 |  |  |  |  | 63 |  | 0
2014-03-08 | 189.865 |  |  |  |  | 0 |  | 0
2014-03-09 | 17.233 |  |  |  |  | 0 |  | 0
2014-03-10 | 17.233 |  |  |  |  | 194 |  | 2
2014-03-11 | 328.604 |  |  |  |  | 159 |  | 0
2014-03-12 | 269.507 |  |  |  |  | 0 |  | 0
2014-03-13 | 180.91 |  |  |  |  | 0 |  | 0
2014-03-14 | 269.496 |  |  |  |  | 78 |  | 0
2014-03-15 | 148.859 |  |  |  |  | 0 |  | 0
2014-03-16 | 244.281 |  |  |  |  | 0 |  | 0
2014-03-17 | 244.281 |  |  |  |  | 0 |  | 19
2014-03-18 | 206.685 |  |  |  |  | 0 |  | 0
2014-03-19 | 207.59 |  |  |  |  | 0 |  | 0
2014-03-20 | 226.4685 |  |  |  |  | 0 |  | 0
2014-03-21 | 226.4685 |  |  |  |  | 0 |  | 0
2014-03-22 | 244.494 |  |  |  |  | 0 |  | 2
2014-03-23 | 251.7225 |  |  |  |  | 0 |  | 0
2014-03-24 | 251.7225 | 7 | 110 | 2 | 93 | 98 | 118 | 0
2014-03-25 | 356.542 |  |  |  |  | 35 |  | 19
2014-03-26 | 388.937 |  |  |  |  | 59 |  | 21
2014-03-27 | 249.726 |  |  |  |  | 0 |  | 4
2014-03-28 | 1269.194 |  |  |  |  | 0 |  | 94
2014-03-29 | 1027.02 |  |  |  |  | 0 |  | 0
2014-03-30 | 427.3965 |  |  |  |  | 0 |  | 0
2014-03-31 | 427.3965 |  |  |  |  | 0 |  | 5
2014-04-01 | 494.365 |  |  |  |  | 0 |  | 0
2014-04-02 | 310.11 |  |  |  |  | 0 |  | 0
2014-04-03 | 245.849 |  |  |  |  | 80 |  | 0
2014-04-04 | 291.659 |  |  |  |  | 0 |  | 0
2014-04-05 | 184.306 |  |  |  |  | 0 |  | 0
2014-04-06 | 527.883 |  |  |  |  | 0 |  | 0
2014-04-07 | 527.883 |  |  |  |  | 0 |  | 28
2014-04-08 | 356.421 |  |  |  |  | 0 |  | 0
2014-04-09 | 278.182 |  |  |  |  | 75 |  | 0
2014-04-10 | 291.536 |  |  |  |  | 0 |  | 0
2014-04-11 | 223.021 |  |  |  |  | 0 |  | 0
2014-04-12 | 231.443 |  |  |  |  | 0 |  | 0
2014-04-13 | 265.577 |  |  |  |  | 0 |  | 0
2014-04-14 | 265.577 |  |  |  |  | 0 |  | 0
2014-04-15 | 327.684 |  |  |  |  | 0 |  | 9
2014-04-16 | 225.681 |  |  |  |  | 0 |  | 0
2014-04-17 | 332.459 |  |  |  |  | 0 |  | 0
2014-04-18 | 201.98 |  |  |  |  | 0 |  | 0
2014-04-19 | 267.812 |  |  |  |  | 0 |  | 0
2014-04-20 | 246.0875 |  |  |  |  | 0 |  | 0
2014-04-21 | 246.0875 | 6 | 54 | 2 | 22 | 104 | 2 | 0
2014-04-22 | 284.922 |  |  |  |  | 0 |  | 0
2014-04-23 | 227.599 |  |  |  |  | 0 |  | 0
2014-04-24 | 213.978 |  |  |  |  | 0 |  | 0
2014-04-25 | 177.564 |  |  |  |  | 0 |  | 0
2014-04-26 | 240.969 |  |  |  |  | 0 |  | 0
2014-04-27 | 548.7435 |  |  |  |  | 0 |  | 0
2014-04-28 | 548.7435 |  |  |  |  | 0 |  | 54
2014-04-29 | 844.801 |  |  |  |  | 0 |  | 1
2014-04-30 | 319.422 |  |  |  |  | 0 |  | 0
2014-05-01 | 423.833 |  |  |  |  | 0 |  | 0
2014-05-02 | 289.593 |  |  |  |  | 0 |  | 4
2014-05-03 | 328.515 |  |  |  |  | 0 |  | 7
2014-05-04 | 372.607 |  |  |  |  | 0 |  | 0
2014-05-05 | 372.607 |  |  |  |  | 0 |  | 0
2014-05-06 | 286.191 |  |  |  |  | 0 |  | 0
2014-05-07 | 253.75 |  |  |  |  | 0 |  | 0
2014-05-08 | 278.177 |  |  |  |  | 0 |  | 4
2014-05-09 | 254.32 |  |  |  |  | 0 |  | 6
2014-05-10 | 76.491 |  |  |  |  | 0 |  | 1
2014-05-11 | 50 |  |  |  |  | 0 |  | 0
2014-05-12 | 50 |  |  |  |  | 0 |  | 1
2014-05-13 | 122.672 |  |  |  |  | 0 |  | 0
2014-05-14 | 263.257 |  |  |  |  | 0 |  | 2
2014-05-15 | 258.97 |  |  |  |  | 0 |  | 1
2014-05-16 | 255.143 |  |  |  |  | 0 |  | 0
2014-05-17 | 260.747 |  |  |  |  | 0 |  | 4
2014-05-18 | 265.332 |  |  |  |  | 0 |  | 2
2014-05-19 | 280.69 | 6 | 12 | 2 | 22 | 0 | 2 | 0
2014-05-20 | 256.272 |  |  |  |  | 0 |  | 0
2014-05-21 | 319.043 |  |  |  |  | 0 |  | 0
2014-05-22 | 162.046 |  |  |  |  | 0 |  | 0
2014-05-23 | 288.519 |  |  |  |  | 0 |  | 0
2014-05-24 | 224.594 |  |  |  |  | 0 |  | 0
2014-05-25 | 258.789 |  |  |  |  | 0 |  | 0
2014-05-26 | 258.789 |  |  |  |  | 0 |  | 0
2014-05-27 | 277.658 |  |  |  |  | 0 |  | 0
2014-05-28 | 212.601 |  |  |  |  | 0 |  | 0
2014-05-29 | 229.288 |  |  |  |  | 0 |  | 0
2014-05-30 | 234.002 |  |  |  |  | 0 |  | 0
2014-05-31 | 243.524 |  |  |  |  | 0 |  | 0
2014-06-01 | 243.524 |  |  |  |  | 0 |  | 0
2014-06-02 | 243.524 |  |  |  |  | 106 |  | 0
2014-06-03 | 269.26 |  |  |  |  | 0 |  | 0
2014-06-04 | 236.826 |  |  |  |  | 0 |  | 0
2014-06-05 | 221.327 |  |  |  |  | 0 |  | 0
2014-06-06 | 177.421 |  |  |  |  | 0 |  | 0
2014-06-07 | 229.675 |  |  |  |  | 0 |  | 0
2014-06-08 | 231.1175 |  |  |  |  | 0 |  | 0
2014-06-09 | 231.1175 |  |  |  |  | 0 |  | 0
2014-06-10 | 251.206 |  |  |  |  | 0 |  | 0
2014-06-11 | 185.409 |  |  |  |  | 0 |  | 0
2014-06-12 | 350.781 |  |  |  |  | 0 |  | 0
2014-06-13 | 145.765 |  |  |  |  | 0 |  | 0
2014-06-14 | 265.874 |  |  |  |  | 0 |  | 0
2014-06-15 | 269.8965 |  |  |  |  | 0 |  | 0
2014-06-16 | 269.8965 | 9 | 160 | 2 | 35 | 0 | 110 | 0
2014-06-17 | 212.361 |  |  |  |  | 0 |  | 0
2014-06-18 | 196.597 |  |  |  |  | 1193 |  | 0
2014-06-19 | 311.155 |  |  |  |  | 0 |  | 0
2014-06-20 | 182.419 |  |  |  |  | 0 |  | 0
2014-06-21 | 229.597 |  |  |  |  | 0 |  | 0
2014-06-22 | 258.974 |  |  |  |  | 0 |  | 0
2014-06-23 | 258.974 |  |  |  |  | 0 |  | 0
2014-06-24 | 296.305 |  |  |  |  | 0 |  | 0
2014-06-25 | 235.606 |  |  |  |  | 0 |  | 0
2014-06-26 | 211.845 |  |  |  |  | 0 |  | 0
2014-06-27 | 210.131 |  |  |  |  | 0 |  | 0
2014-06-28 | 180.661 |  |  |  |  | 0 |  | 0
2014-06-29 | 133.6685 |  |  |  |  | 0 |  | 0
2014-06-30 | 133.6685 |  |  |  |  | 0 |  | 0
2014-07-01 | 374.404 |  |  |  |  | 0 |  | 0
2014-07-02 | 241.321 |  |  |  |  | 0 |  | 0
2014-07-03 | 227.471 |  |  |  |  | 0 |  | 0
2014-07-04 | 220.504 |  |  |  |  | 0 |  | 0
2014-07-05 | 194.208 |  |  |  |  | 0 |  | 0
2014-07-06 | 226.994 |  |  |  |  | 0 |  | 0
2014-07-07 | 226.994 |  |  |  |  | 0 |  | 0
2014-07-08 | 221.823 |  |  |  |  | 0 |  | 0
2014-07-09 | 197.315 |  |  |  |  | 0 |  | 0
2014-07-10 | 202.416 |  |  |  |  | 95 |  | 0
2014-07-11 | 281.036 |  |  |  |  | 0 |  | 0
2014-07-12 | 216.965 |  |  |  |  | 0 |  | 0
2014-07-13 | 184.3145 |  |  |  |  | 0 |  | 0
2014-07-14 | 184.3145 | 4 | 30 | 2 | 6 | 347 | 170 | 0
2014-07-15 | 267.49 |  |  |  |  | 0 |  | 5
2014-07-16 | 203.397 |  |  |  |  | 0 |  | 1
2014-07-17 | 237.396 |  |  |  |  | 0 |  | 0
2014-07-18 | 196.795 |  |  |  |  | 0 |  | 0
2014-07-19 | 199.797 |  |  |  |  | 0 |  | 0
2014-07-20 | 243.5605 |  |  |  |  | 0 |  | 0
2014-07-21 | 243.5605 |  |  |  |  | 0 |  | 2
2014-07-22 | 241.724 |  |  |  |  | 0 |  | 0
2014-07-23 | 203.592 |  |  |  |  | 0 |  | 0
2014-07-24 | 232.252 |  |  |  |  | 0 |  | 0
2014-07-25 | 233.235 |  |  |  |  | 85 |  | 0
2014-07-26 | 208.695 |  |  |  |  | 0 |  | 0
2014-07-27 | 243.3725 |  |  |  |  | 0 |  | 0
2014-07-28 | 243.3725 |  |  |  |  | 94 |  | 0
2014-07-29 | 201.68 |  |  |  |  | 57 |  | 0
2014-07-30 | 262.526 |  |  |  |  | 52 |  | 0
2014-07-31 | 173.103 |  |  |  |  | 85 |  | 0
2014-08-01 | 218.399 |  |  |  |  | 123 |  | 0
2014-08-02 | 188.897 |  |  |  |  | 56 |  | 0
2014-08-03 | 248.9675 |  |  |  |  | 0 |  | 0
2014-08-04 | 248.9675 |  |  |  |  | 54 |  | 17
2014-08-05 | 269.97 |  |  |  |  | 0 |  | 1
2014-08-06 | 228.472 |  |  |  |  | 0 |  | 0
2014-08-07 | 176.778 |  |  |  |  | 219 |  | 0
2014-08-08 | 225.294 |  |  |  |  | 118 |  | 0
2014-08-09 | 182.124 |  |  |  |  | 0 |  | 0
2014-08-10 | 258.9175 |  |  |  |  | 0 |  | 0
2014-08-11 | 491.8405 |  |  |  |  | 98 |  | 0
2014-08-12 | 491.8405 | 3 | 220 | 2 | 5 | 80 | 2 | 0
2014-08-13 | 220.836 |  |  |  |  | 98 |  | 0
2014-08-14 | 224.103 |  |  |  |  | 91 |  | 1
2014-08-15 | 224.049 |  |  |  |  | 0 |  | 0
2014-08-16 | 197.726 |  |  |  |  | 0 |  | 0
2014-08-17 | 406.7975 |  |  |  |  | 0 |  | 0
2014-08-18 | 334.9042 |  |  |  |  | 0 |  | 0
2014-08-19 | 334.9042 |  |  |  |  | 0 |  | 0
2014-08-20 | 218.301 |  |  |  |  | 0 |  | 0
2014-08-21 | 207.581 |  |  |  |  | 0 |  | 3
2014-08-22 | 453.96 |  |  |  |  | 0 |  | 20
2014-08-23 | 932.412 |  |  |  |  | 0 |  | 54
2014-08-24 | 1455.893 |  |  |  |  | 0 |  | 0
2014-08-25 | 980.0015 |  |  |  |  | 0 |  | 24
2014-08-26 | 980.0015 |  |  |  |  | 0 |  | 1
2014-08-27 | 480.807 |  |  |  |  | 0 |  | 11
2014-08-28 | 1869.573 |  |  |  |  | 0 |  | 97
2014-08-29 | 1383.301 |  |  |  |  | 0 |  | 0
2014-08-30 | 681.369 |  |  |  |  | 0 |  | 0
2014-08-31 | 553.575 |  |  |  |  | 0 |  | 0
MINIMUM | 17.233 | 3 | 2 | 2 | 5 | 0 | 2 | 0
AVERAGE | 281.7482 | 7.8462 | 93.8462 | 2 | 46.8462 | 62.2308 | 32.1538 | 2.3507
MAXIMUM | 1869.573 | 18 | 240 | 2 | 100 | 930 | 170 | 97
| 102838.0915 |  |  |  |  | 12471 |  | 858
| SAMPLE COUNT | 13

## 14-15
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 14/15
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring |  |  |  | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | 1000 | -
2014-09-01 | 553.58 |  |  |  |  | 0 |  | 0
2014-09-02 | 509.454 |  |  |  |  | 0 |  | 0
2014-09-03 | 385.416 |  |  |  |  | 0 |  | 0
2014-09-04 | 365.989 |  |  |  |  | 0 |  | 0
2014-09-05 | 302.802 |  |  |  |  | 0 |  | 0
2014-09-06 | 275.811 |  |  |  |  | 0 |  | 0
2014-09-07 | 354.862 |  |  |  |  | 0 |  | 0
2014-09-08 | 354.862 | 3 | 14 | 2 | 10 | 46 | 1 | 6
2014-09-09 | 421.631 |  |  |  |  | 46 |  | 5
2014-09-10 | 251.13 |  |  |  |  | 0 |  | 0
2014-09-11 | 398.545 |  |  |  |  | 0 |  | 0
2014-09-12 | 289.15 |  |  |  |  | 0 |  | 0
2014-09-13 | 279.416 |  |  |  |  | 0 |  | 0
2014-09-14 | 293.966 |  |  |  |  | 0 |  | 0
2014-09-15 | 293.966 |  |  |  |  | 0 |  | 0
2014-09-16 | 339.033 |  |  |  |  | 0 |  | 3
2014-09-17 | 222.02 |  |  |  |  | 0 |  | 0
2014-09-18 | 222.704 |  |  |  |  | 0 |  | 0
2014-09-19 | 275.522 |  |  |  |  | 0 |  | 0
2014-09-20 | 229.708 |  |  |  |  | 0 |  | 0
2014-09-21 | 288.952 |  |  |  |  | 0 |  | 0
2014-09-22 | 288.952 |  |  |  |  | 0 |  | 2
2014-09-23 | 267.29 |  |  |  |  | 107 |  | 0
2014-09-24 | 272.924 |  |  |  |  | 37 |  | 0
2014-09-25 | 232.816 |  |  |  |  | 163 |  | 1
2014-09-26 | 245.61 |  |  |  |  | 0 |  | 0
2014-09-27 | 226.39 |  |  |  |  | 54 |  | 1
2014-09-28 | 350.6273 |  |  |  |  | 0 |  | 0
2014-09-29 | 350.6273 |  |  |  |  | 0 |  | 1
2014-09-30 | 350.6273 |  |  |  |  | 79 |  | 0
2014-10-01 | 338.6588 |  |  |  |  | 57 |  | 0
2014-10-02 | 325.487 |  |  |  |  | 144 |  | 0
2014-10-03 | 305.288 |  |  |  |  | 273 |  | 0
2014-10-04 | 293.5408 |  |  |  |  | 42 |  | 0
2014-10-05 | 243.0505 |  |  |  |  | 88 |  | 0
2014-10-06 | 243.0505 | 3 | 20 | 2 | 13 | 0 | 172 | 0
2014-10-07 | 260.744 |  |  |  |  | 87 |  | 0
2014-10-08 | 276.491 |  |  |  |  | 86 |  | 0
2014-10-09 | 267.317 |  |  |  |  | 221 |  | 0
2014-10-10 | 202.831 |  |  |  |  | 204 |  | 0
2014-10-11 | 270.964 |  |  |  |  | 0 |  | 0
2014-10-12 | 323.3577 |  |  |  |  | 90 |  | 0
2014-10-13 | 323.3577 |  |  |  |  | 0 |  | 0
2014-10-14 | 323.3577 |  |  |  |  | 78 |  | 0
2014-10-15 | 337.9682 |  |  |  |  | 217 |  | 0
2014-10-16 | 336.496 |  |  |  |  | 94 |  | 0
2014-10-17 | 303.1233 |  |  |  |  | 220 |  | 0
2014-10-18 | 321.7847 |  |  |  |  | 47 |  | 0
2014-10-19 | 243.128 |  |  |  |  | 0 |  | 0
2014-10-20 | 243.128 |  |  |  |  | 0 |  | 0
2014-10-21 | 243.128 |  |  |  |  | 153 |  | 0
2014-10-22 | 228.386 |  |  |  |  | 61 |  | 0
2014-10-23 | 224.518 |  |  |  |  | 226 |  | 0
2014-10-24 | 169.189 |  |  |  |  | 208 |  | 0
2014-10-25 | 216.579 |  |  |  |  | 121 |  | 0
2014-10-26 | 231.0365 |  |  |  |  | 0 |  | 0
2014-10-27 | 231.0365 |  |  |  |  | 0 |  | 0
2014-10-28 | 309.572 |  |  |  |  | 154 |  | 0
2014-10-29 | 211.045 |  |  |  |  | 54 |  | 0
2014-10-30 | 178.99 |  |  |  |  | 273 |  | 0
2014-10-31 | 187.523 |  |  |  |  | 133 |  | 0
2014-11-01 | 207.893 |  |  |  |  | 0 |  | 0
2014-11-02 | 254.407 |  |  |  |  | 0 |  | 0
2014-11-03 | 254.407 | 11 | 61 | 2 | 16 | 0 | 2 | 0
2014-11-04 | 218.802 |  |  |  |  | 0 |  | 0
2014-11-05 | 232.385 |  |  |  |  | 0 |  | 0
2014-11-06 | 252.335 |  |  |  |  | 239 |  | 16
2014-11-07 | 208.345 |  |  |  |  | 211 |  | 9
2014-11-08 | 195.474 |  |  |  |  | 68 |  | 0
2014-11-09 | 216.061 |  |  |  |  | 0 |  | 0
2014-11-10 | 216.061 |  |  |  |  | 0 |  | 0
2014-11-11 | 292.944 |  |  |  |  | 203 |  | 0
2014-11-12 | 180.834 |  |  |  |  | 138 |  | 2
2014-11-13 | 241.562 |  |  |  |  | 0 |  | 0
2014-11-14 | 216.005 |  |  |  |  | 0 |  | 0
2014-11-15 | 151.849 |  |  |  |  | 0 |  | 0
2014-11-16 | 258.4215 |  |  |  |  | 0 |  | 0
2014-11-17 | 258.4215 |  |  |  |  | 0 |  | 0
2014-11-18 | 149.007 |  |  |  |  | 0 |  | 0
2014-11-19 | 293.056 |  |  |  |  | 303 |  | 3
2014-11-20 | 229.831 |  |  |  |  | 63 |  | 0
2014-11-21 | 177.169 |  |  |  |  | 83 |  | 0
2014-11-22 | 227.302 |  |  |  |  | 70 |  | 0
2014-11-23 | 238.064 |  |  |  |  | 0 |  | 0
2014-11-24 | 238.064 |  |  |  |  | 0 |  | 0
2014-11-25 | 213.035 |  |  |  |  | 116 |  | 0
2014-11-26 | 241.607 |  |  |  |  | 87 |  | 7
2014-11-27 | 231.815 |  |  |  |  | 307 |  | 0
2014-11-28 | 269.117 |  |  |  |  | 95 |  | 17
2014-11-29 | 170.863 |  |  |  |  | 46 |  | 0
2014-11-30 | 265.2395 |  |  |  |  | 0 |  | 0
2014-12-01 | 265.2395 | 5 | 42 | 2 | 26 | 0 | 30 | 0
2014-12-02 | 221.406 |  |  |  |  | 102 |  | 0
2014-12-03 | 189.077 |  |  |  |  | 0 |  | 0
2014-12-04 | 279.89 |  |  |  |  | 0 |  | 0
2014-12-05 | 299.474 |  |  |  |  | 0 |  | 35
2014-12-06 | 220.154 |  |  |  |  | 0 |  | 1
2014-12-07 | 296.4315 |  |  |  |  | 0 |  | 0
2014-12-08 | 296.4315 |  |  |  |  | 0 |  | 1
2014-12-09 | 282.09 |  |  |  |  | 0 |  | 32
2014-12-10 | 317.9 |  |  |  |  | 0 |  | 0
2014-12-11 | 212.943 |  |  |  |  | 0 |  | 0
2014-12-12 | 357.609 |  |  |  |  | 0 |  | 14
2014-12-13 | 213.118 |  |  |  |  | 0 |  | 3
2014-12-14 | 315.5705 |  |  |  |  | 0 |  | 0
2014-12-15 | 315.5705 |  |  |  |  | 0 |  | 8
2014-12-16 | 244.6235 |  |  |  |  | 0 |  | 0
2014-12-17 | 244.6235 |  |  |  |  | 0 |  | 5
2014-12-18 | 283.931 |  |  |  |  | 0 |  | 2
2014-12-19 | 245.487 |  |  |  |  | 0 |  | 15
2014-12-20 | 229.096 |  |  |  |  | 0 |  | 0
2014-12-21 | 233.612 |  |  |  |  | 0 |  | 0
2014-12-22 | 233.612 |  |  |  |  | 0 |  | 0
2014-12-23 | 165.654 |  |  |  |  | 0 |  | 0
2014-12-24 | 240.817 |  |  |  |  | 143 |  | 0
2014-12-25 | 194.063 |  |  |  |  | 0 |  | 0
2014-12-26 | 194.063 |  |  |  |  | 0 |  | 0
2014-12-27 | 229.72 |  |  |  |  | 0 |  | 11
2014-12-28 | 1025.791 |  |  |  |  | 0 |  | 0
2014-12-29 | 1025.791 |  |  |  |  | 0 |  | 91
2014-12-30 | 406.551 |  |  |  |  | 0 |  | 0
2014-12-31 | 354.92 |  |  |  |  | 0 |  | 0
2015-01-01 | 280.834 |  |  |  |  | 0 |  | 0
2015-01-02 | 295.815 |  |  |  |  | 0 |  | 1
2015-01-03 | 275.313 |  |  |  |  | 80 |  | 0
2015-01-04 | 281.561 |  |  |  |  | 0 |  | 0
2015-01-05 | 281.561 | 10 | 140 | 2 | 60 | 0 |  | 1
2015-01-06 | 374.804 |  |  |  |  | 0 |  | 5
2015-01-07 | 249.871 |  |  |  |  | 178 |  | 0
2015-01-08 | 286.792 |  |  |  |  | 0 |  | 2
2015-01-09 | 281.198 |  |  |  |  | 108 |  | 0
2015-01-10 | 190.765 |  |  |  |  | 0 |  | 0
2015-01-11 | 312.8435 |  |  |  |  | 0 |  | 0
2015-01-12 | 312.8435 |  |  |  |  | 0 |  | 3
2015-01-13 | 248.005 |  |  |  |  | 106 | 10 | 0
2015-01-14 | 330.314 |  |  |  |  | 0 |  | 2
2015-01-15 | 253.462 |  |  |  |  | 59 |  | 0
2015-01-16 | 187.481 |  |  |  |  | 103 |  | 0
2015-01-17 | 212.738 |  |  |  |  | 0 |  | 0
2015-01-18 | 239.216 |  |  |  |  | 0 |  | 0
2015-01-19 | 239.216 |  |  |  |  | 0 |  | 0
2015-01-20 | 300.418 |  |  |  |  | 0 |  | 5
2015-01-21 | 232.548 |  |  |  |  | 0 |  | 0
2015-01-22 | 225.177 |  |  |  |  | 73 |  | 5
2015-01-23 | 258 |  |  |  |  | 0 |  | 0
2015-01-24 | 258 |  |  |  |  | 0 |  | 0
2015-01-25 | 258 |  |  |  |  | 0 |  | 0
2015-01-26 | 258 |  |  |  |  | 0 |  | 0
2015-01-27 | 258 | 5 | 188 | 2 | 32 | 0 | 192 | 0
2015-01-28 | 258 |  |  |  |  | 0 |  | 0
2015-01-29 | 258 |  |  |  |  | 0 |  | 0
2015-01-30 | 258 |  |  |  |  | 0 |  | 0
2015-01-31 | 258 |  |  |  |  | 0 |  | 0
2015-02-01 | 258 |  |  |  |  | 0 |  | 0
2015-02-02 | 258 |  |  |  |  | 0 |  | 3
2015-02-03 | 262.421 |  |  |  |  | 0 |  | 7.5
2015-02-04 | 455.136 |  |  |  |  | 0 |  | 13
2015-02-05 | 320.676 |  |  |  |  | 0 |  | 2
2015-02-06 | 243.894 |  |  |  |  | 44 |  | 1
2015-02-07 | 305.155 |  |  |  |  | 0 |  | 0
2015-02-08 | 277.411 |  |  |  |  | 0 |  | 0
2015-02-09 | 277.414 |  |  |  |  | 0 |  | 0
2015-02-10 | 266.151 |  |  |  |  | 0 |  | 7.5
2015-02-11 | 286.471 |  |  |  |  | 0 |  | 2.5
2015-02-12 | 280.67 |  |  |  |  | 0 |  | 5
2015-02-13 | 283.92 |  |  |  |  | 0 |  | 5.5
2015-02-14 | 233.728 |  |  |  |  | 0 |  | 0
2015-02-15 | 275.45 |  |  |  |  | 0 |  | 0
2015-02-16 | 275.453 |  |  |  |  | 0 |  | 0
2015-02-17 | 237.371 |  |  |  |  | 0 |  | 0
2015-02-18 | 298.422 |  |  |  |  | 0 |  | 1
2015-02-19 | 270.656 |  |  |  |  | 0 |  | 8
2015-02-20 | 452.219 |  |  |  |  | 0 |  | 40
2015-02-21 | 958.3 |  |  |  |  | 0 |  | 0
2015-02-22 | 958.297 |  |  |  |  | 0 |  | 0
2015-02-23 | 1274.399 |  |  |  |  | 0 |  | 14
2015-02-24 | 972.95 | 4 | 3500 | 2 | 4 | 0 |  | 0
2015-02-25 | 656.292 |  |  |  |  | 0 |  | 0
2015-02-26 | 489.756 |  |  |  |  | 0 |  | 0
2015-02-27 | 417.16 |  |  |  |  | 0 |  | 1
2015-02-28 | 414.733 |  |  |  |  | 0 |  | 0
2015-03-01 | 389.9435 |  |  |  |  | 0 |  | 0
2015-03-02 | 389.9435 |  |  |  |  | 0 |  | 3
2015-03-03 | 648.892 |  |  |  |  | 0 |  | 7
2015-03-04 | 307.328 |  |  |  |  | 0 |  | 0
2015-03-05 | 152.267 |  |  |  |  | 0 |  | 0
2015-03-06 | 152.267 |  |  |  |  | 0 |  | 0
2015-03-07 | 323.686 |  |  |  |  | 0 |  | 0
2015-03-08 | 276.7405 |  |  |  |  | 0 |  | 0
2015-03-09 | 276.7405 |  |  |  |  | 0 |  | 0
2015-03-10 | 281.485 |  |  |  |  | 117 |  | 5
2015-03-11 | 276.74 |  |  |  |  | 0 |  | 0
2015-03-12 | 256.233 |  |  |  |  | 0 |  | 0
2015-03-13 | 309.819 |  |  |  |  | 0 |  | 0
2015-03-14 | 246.378 |  |  |  |  | 0 |  | 4
2015-03-15 | 254.0475 |  |  |  |  | 0 |  | 0
2015-03-16 | 254.0475 |  |  |  |  | 0 |  | 3
2015-03-17 | 254.574 |  |  |  |  | 0 |  | 0
2015-03-18 | 269.924 |  |  |  |  | 0 |  | 4
2015-03-19 | 275.248 |  |  |  |  | 95 |  | 2.5
2015-03-20 | 245.154 |  |  |  |  | 0 |  | 0
2015-03-21 | 246.246 |  |  |  |  | 50 |  | 0
2015-03-22 | 323.6025 |  |  |  |  | 0 |  | 0
2015-03-23 | 323.6025 |  |  |  |  | 246 |  | 26
2015-03-24 | 295.057 | 6 | 192 | 2 | 17 | 242 | 1 | 0
2015-03-25 | 283.529 |  |  |  |  | 172 |  | 0
2015-03-26 | 288.98 |  |  |  |  | 288 |  | 0
2015-03-27 | 331.855 |  |  |  |  | 0 |  | 8
2015-03-28 | 211.89 |  |  |  |  | 0 |  | 0
2015-03-29 | 277.054 |  |  |  |  | 0 |  | 0
2015-03-30 | 277.054 |  |  |  |  | 0 |  | 0
2015-03-31 | 257.645 |  |  |  |  | 0 |  | 0
2015-04-01 | 350.896 |  |  |  |  | 0 |  | 16
2015-04-02 | 350.378 |  |  |  |  | 213 |  | 7
2015-04-03 | 306.775 |  |  |  |  | 0 |  | 10
2015-04-04 | 935.191 |  |  |  |  | 0 |  | 56
2015-04-05 | 1502.5255 |  |  |  |  | 0 |  | 0
2015-04-06 | 1502.5255 |  |  |  |  | 0 |  | 26
2015-04-07 | 621.784 |  |  |  |  | 0 |  | 3
2015-04-08 | 544.118 |  |  |  |  | 0 |  | 0
2015-04-09 | 322.762 |  |  |  |  | 0 |  | 0
2015-04-10 | 430.13 |  |  |  |  | 0 |  | 0
2015-04-11 | 309.965 |  |  |  |  | 0 |  | 0
2015-04-12 | 301.298 |  |  |  |  | 0 |  | 0
2015-04-13 | 301.298 |  |  |  |  | 0 |  | 0
2015-04-14 | 304.469 |  |  |  |  | 132 |  | 0
2015-04-15 | 288.693 |  |  |  |  | 0 |  | 0
2015-04-16 | 296.297 |  |  |  |  | 0 |  | 0
2015-04-17 | 282.882 |  |  |  |  | 0 |  | 0
2015-04-18 | 306.753 |  |  |  |  | 0 |  | 0
2015-04-19 | 270.668 |  |  |  |  | 0 |  | 0
2015-04-20 | 270.668 |  |  |  |  | 142 |  | 8
2015-04-21 | 306.35 | 4 | 100 | 2 | 33 | 0 | 2 | 3
2015-04-22 | 298.789 |  |  |  |  | 0 |  | 0
2015-04-23 | 276.116 |  |  |  |  | 0 |  | 0
2015-04-24 | 330.419 |  |  |  |  | 0 |  | 0
2015-04-25 | 264.822 |  |  |  |  | 0 |  | 0
2015-04-26 | 274.5285 |  |  |  |  | 0 |  | 0
2015-04-27 | 274.5285 |  |  |  |  | 0 |  | 0
2015-04-28 | 293.804 |  |  |  |  | 0 |  | 0
2015-04-29 | 265.177 |  |  |  |  | 0 |  | 2
2015-04-30 | 272.843 |  |  |  |  | 0 |  | 8
2015-05-01 | 829.077 |  |  |  |  | 0 |  | 47
2015-05-02 | 2792.022 |  |  |  |  | 0 |  | 190
2015-05-03 | 1243.945 |  |  |  |  | 0 |  | 0
2015-05-04 | 1243.945 |  |  |  |  | 0 |  | 0
2015-05-05 | 889.073 |  |  |  |  | 0 |  | 0
2015-05-06 | 715.785 |  |  |  |  | 0 |  | 0
2015-05-07 | 563.029 |  |  |  |  | 0 |  | 0
2015-05-08 | 643.843 |  |  |  |  | 0 |  | 0
2015-05-09 | 445.236 |  |  |  |  | 0 |  | 0
2015-05-10 | 431.4995 |  |  |  |  | 0 |  | 0
2015-05-11 | 431.4995 |  |  |  |  | 0 |  | 0
2015-05-12 | 416.393 |  |  |  |  | 0 |  | 0
2015-05-13 | 431.51 |  |  |  |  | 0 |  | 0
2015-05-14 | 380.769 |  |  |  |  | 0 |  | 0
2015-05-15 | 366.207 |  |  |  |  | 0 |  | 0
2015-05-16 | 442.57 |  |  |  |  | 0 |  | 0
2015-05-17 | 426.755 |  |  |  |  | 0 |  | 0
2015-05-18 | 426.755 | 4 | 62 | 2 | 8 | 62 | 1 | 22
2015-05-19 | 431.91 |  |  |  |  | 0 |  | 3
2015-05-20 | 415.594 |  |  |  |  | 0 |  | 0
2015-05-21 | 372.878 |  |  |  |  | 0 |  | 0
2015-05-22 | 567.294 |  |  |  |  | 0 |  | 11
2015-05-23 | 337.763 |  |  |  |  | 0 |  | 0
2015-05-24 | 368.258 |  |  |  |  | 0 |  | 0
2015-05-25 | 368.258 |  |  |  |  | 0 |  | 2
2015-05-26 | 351.6 |  |  |  |  | 0 |  | 1
2015-05-27 | 351.517 |  |  |  |  | 0 |  | 0
2015-05-28 | 336.593 |  |  |  |  | 0 |  | 0
2015-05-29 | 308.425 |  |  |  |  | 0 |  | 0
2015-05-30 | 303.415 |  |  |  |  | 0 |  | 0
2015-05-31 | 318.5335 |  |  |  |  | 0 |  | 0
2015-06-01 | 318.5335 |  |  |  |  | 0 |  | 0
2015-06-02 | 304.27 |  |  |  |  | 0 |  | 0
2015-06-03 | 295.01 |  |  |  |  | 0 |  | 0
2015-06-04 | 294.261 |  |  |  |  | 0 |  | 0
2015-06-05 | 340.841 |  |  |  |  | 0 |  | 0
2015-06-06 | 240.365 |  |  |  |  | 0 |  | 2
2015-06-07 | 281.2455 |  |  |  |  | 0 |  | 0
2015-06-08 | 281.2455 |  |  |  |  | 0 |  | 3
2015-06-09 | 277.815 |  |  |  |  | 0 |  | 0
2015-06-10 | 272.507 |  |  |  |  | 77 |  | 0
2015-06-11 | 291.668 |  |  |  |  | 0 |  | 0
2015-06-12 | 284.717 |  |  |  |  | 0 |  | 0
2015-06-13 | 348.167 |  |  |  |  | 0 |  | 10
2015-06-14 | 362.202 |  |  |  |  | 0 |  | 0
2015-06-15 | 362.202 |  |  |  |  | 178 |  | 4
2015-06-16 | 305.249 | 2 | 10 | 3.6 | 4 | 0 | 2 | 3
2015-06-17 | 355.208 |  |  |  |  | 0 |  | 9
2015-06-18 | 366.664 |  |  |  |  | 0 |  | 0
2015-06-19 | 388.263 |  |  |  |  | 0 |  | 0
2015-06-20 | 330.476 |  |  |  |  | 0 |  | 0
2015-06-21 | 270.527 |  |  |  |  | 0 |  | 0
2015-06-22 | 270.527 |  |  |  |  | 192 |  | 0
2015-06-23 | 289.792 |  |  |  |  | 0 |  | 0
2015-06-24 | 281.125 |  |  |  |  | 0 |  | 0
2015-06-25 | 291.716 |  |  |  |  | 0 |  | 2
2015-06-26 | 291.404 |  |  |  |  | 0 |  | 2
2015-06-27 | 309.864 |  |  |  |  | 0 |  | 2
2015-06-28 | 273.32 |  |  |  |  | 0 |  | 0
2015-06-29 | 273.32 |  |  |  |  | 0 |  | 0
2015-06-30 | 272.515 |  |  |  |  | 0 |  | 1
2015-07-01 | 284.144 |  |  |  |  | 0 |  | 0
2015-07-02 | 275.338 |  |  |  |  | 0 |  | 0
2015-07-03 | 355.132 |  |  |  |  | 0 |  | 0
2015-07-04 | 242.394 |  |  |  |  | 0 |  | 0
2015-07-05 | 282.827 |  |  |  |  | 0 |  | 0
2015-07-06 | 282.827 |  |  |  |  | 0 |  | 0
2015-07-07 | 210.558 |  |  |  |  | 0 |  | 0
2015-07-08 | 268.834 |  |  |  |  | 0 |  | 0
2015-07-09 | 254.535 |  |  |  |  | 0 |  | 0
2015-07-10 | 361.611 |  |  |  |  | 0 |  | 0
2015-07-11 | 187.737 |  |  |  |  | 0 |  | 0
2015-07-12 | 270.395 |  |  |  |  | 0 |  | 0
2015-07-13 | 270.395 |  |  |  |  | 0 |  | 0
2015-07-14 | 256.37 | 2 | 68 | 2 | 7 | 88 | 2 | 0
2015-07-15 | 265.543 |  |  |  |  | 0 |  | 0
2015-07-16 | 275.175 |  |  |  |  | 0 |  | 0
2015-07-17 | 291.627 |  |  |  |  | 0 |  | 0
2015-07-18 | 191.096 |  |  |  |  | 0 |  | 0
2015-07-19 | 260.9775 |  |  |  |  | 0 |  | 0
2015-07-20 | 260.9775 |  |  |  |  | 0 |  | 3
2015-07-21 | 276.2 |  |  |  |  | 0 |  | 8
2015-07-22 | 273.555 |  |  |  |  | 0 |  | 0
2015-07-23 | 278.303 |  |  |  |  | 0 |  | 0
2015-07-24 | 265.091 |  |  |  |  | 0 |  | 0
2015-07-25 | 387.27 |  |  |  |  | 0 |  | 12
2015-07-26 | 273.896 |  |  |  |  | 0 |  | 0
2015-07-27 | 273.896 |  |  |  |  | 0 |  | 0
2015-07-28 | 281.269 |  |  |  |  | 0 |  | 0
2015-07-29 | 273.432 |  |  |  |  | 0 |  | 0
2015-07-30 | 272.343 |  |  |  |  | 0 |  | 0
2015-07-31 | 308.839 |  |  |  |  | 0 |  | 0
2015-08-01 | 244.673 |  |  |  |  | 0 |  | 0
2015-08-02 | 256.2155 |  |  |  |  | 0 |  | 0
2015-08-03 | 256.2155 |  |  |  |  | 0 |  | 0
2015-08-04 | 257.146 |  |  |  |  | 0 |  | 0
2015-08-05 | 258.104 |  |  |  |  | 0 |  | 0
2015-08-06 | 257.955 |  |  |  |  | 0 |  | 0
2015-08-07 | 264.844 |  |  |  |  | 114 |  | 0
2015-08-08 | 284.051 |  |  |  |  | 0 |  | 0
2015-08-09 | 272.0785 |  |  |  |  | 0 |  | 0
2015-08-10 | 272.0785 |  |  |  |  | 100 | 2 | 0
2015-08-11 | 206.149 | 2 | 16 | 2 | 10 | 0 |  | 0
2015-08-12 | 268.084 |  |  |  |  | 126 |  | 0
2015-08-13 | 248.543 |  |  |  |  | 0 |  | 0
2015-08-14 | 311.614 |  |  |  |  | 0 |  | 0
2015-08-15 | 219.665 |  |  |  |  | 0 |  | 0
2015-08-16 | 246.5525 |  |  |  |  | 0 |  | 0
2015-08-17 | 246.5525 |  |  |  |  | 210 |  | 2.5
2015-08-18 | 251.79 |  |  |  |  | 0 |  | 0
2015-08-19 | 251.79 |  |  |  |  | 105 |  | 0
2015-08-20 | 237.25 |  |  |  |  | 0 |  | 2
2015-08-21 | 301.641 |  |  |  |  | 0 |  | 0
2015-08-22 | 165.347 |  |  |  |  | 0 |  | 3
2015-08-23 | 260.0155 |  |  |  |  | 0 |  | 0
2015-08-24 | 260.0155 |  |  |  |  | 0 |  | 0
2015-08-25 | 287.223 |  |  |  |  | 0 |  | 22
2015-08-26 | 287.223 |  |  |  |  | 0 |  | 0
2015-08-27 | 250.036 |  |  |  |  | 0 |  | 1
2015-08-28 | 307.709 |  |  |  |  | 0 |  | 6
2015-08-29 | 229.392 |  |  |  |  | 0 |  | 0
2015-08-30 | 240.9685 |  |  |  |  | 0 |  | 0
2015-08-31 | 240.9685 |  |  |  |  | 204 |  | 0
MINIMUM | 149.007 | 2 | 10 | 2 | 4 | 0 | 1 | 0
AVERAGE | 327.3049 | 4.6923 | 339.4615 | 2.1231 | 18.4615 | 46.1154 | 34.75 | 2.7425
MAXIMUM | 2792.022 | 11 | 3500 | 3.6 | 60 | 307 | 192 | 190
| 119466.3008 |  |  |  |  | 10041 |  | 1001
| SAMPLE COUNT | 13

## 15-16
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 15/16
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Date analysis results obtained | Date Published
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2015-09-01 | 259.28 | [6 empty] | 120 |  | 0
2015-09-02 | 245.043 | [6 empty] | 0 |  | 0
2015-09-03 | 265.451 | [6 empty] | 0 |  | 6
2015-09-04 | 238.976 | [6 empty] | 0 |  | 0
2015-09-05 | 281.531 | [6 empty] | 0 |  | 0
2015-09-06 | 236.177 | [6 empty] | 0 |  | 0
2015-09-07 | 236.177 | 4 | 50 | 2 | 13 | 12 | 3.3 | 68 | 2 | 3 | 2015-09-15 | 2015-09-29
2015-09-08 | 295.401 | [6 empty] | 0 |  | 3
2015-09-09 | 251.844 | [6 empty] | 0 |  | 2
2015-09-10 | 230.002 | [6 empty] | 0 |  | 0
2015-09-11 | 266.237 | [6 empty] | 0 |  | 1
2015-09-12 | 203.832 | [6 empty] | 0 |  | 0
2015-09-13 | 264.422 | [6 empty] | 0 |  | 0
2015-09-14 | 264.422 | [6 empty] | 0 |  | 0
2015-09-15 | 243.369 | [6 empty] | 219 |  | 0
2015-09-16 | 178.928 | [6 empty] | 113 |  | 0
2015-09-17 | 233.539 | [6 empty] | 444 |  | 12
2015-09-18 | 314.116 | [6 empty] | 0 |  | 30
2015-09-19 | 394.232 | [6 empty] | 0 |  | 6
2015-09-20 | 236.1365 | [6 empty] | 0 |  | 0
2015-09-21 | 236.1365 | [6 empty] | 0 |  | 7
2015-09-22 | 249.023 | [6 empty] | 0 |  | 0
2015-09-23 | 234.948 | [6 empty] | 0 |  | 0
2015-09-24 | 229.246 | [6 empty] | 0 |  | 0
2015-09-25 | 273.8 | [6 empty] | 0 |  | 0
2015-09-26 | 203.326 | [6 empty] | 0 |  | 2
2015-09-27 | 228.853 | [6 empty] | 0 |  | 0
2015-09-28 | 228.853 | [6 empty] | 312 |  | 9
2015-09-29 | 250.48 | [6 empty] | 0 |  | 0
2015-09-30 | 240.694 | [6 empty] | 0 |  | 0
2015-10-01 | 167.084 | [6 empty] | 0 |  | 0
2015-10-02 | 316.8467 | [6 empty] | 71 |  | 0
2015-10-03 | 313.8297 | [6 empty] | 0 |  | 0
2015-10-04 | 335.3493 | [6 empty] | 0 |  | 0
2015-10-05 | 231.643 | 4 | 90 | 2 | 16 | 10 | 3.35 | 57 | 2 | 0 | 2015-10-12 | 2015-10-23
2015-10-06 | 190.616 | [6 empty] | 293 |  | 0
2015-10-07 | 214.454 | [6 empty] | 0 |  | 0
2015-10-08 | 213.088 | [6 empty] | 0 |  | 0
2015-10-09 | 255.344 | [6 empty] | 0 |  | 3
2015-10-10 | 173.624 | [6 empty] | 0 |  | 0
2015-10-11 | 255.8135 | [6 empty] | 0 |  | 0
2015-10-12 | 255.8135 | [6 empty] | 0 |  | 0
2015-10-13 | 240.458 | [6 empty] | 0 |  | 0
2015-10-14 | 141.636 | [6 empty] | 0 |  | 0
2015-10-15 | 227.801 | [6 empty] | 0 |  | 0
2015-10-16 | 270.4287 | [6 empty] | 0 |  | 0
2015-10-17 | 301.2795 | [6 empty] | 0 |  | 0
2015-10-18 | 303.4087 | [6 empty] | 0 |  | 0
2015-10-19 | 234.1885 | [6 empty] | 270 |  | 0
2015-10-20 | 237.355 | [6 empty] | 199 |  | 0
2015-10-21 | 219.191 | [6 empty] | 0 |  | 0
2015-10-22 | 216.412 | [6 empty] | 0 |  | 0
2015-10-23 | 251.637 | [6 empty] | 0 |  | 0
2015-10-24 | 183.609 | [6 empty] | 0 |  | 0
2015-10-25 | 223.8645 | [6 empty] | 0 |  | 0
2015-10-26 | 223.8645 | [6 empty] | 0 |  | 0
2015-10-27 | 245.118 | [6 empty] | 0 |  | 0
2015-10-28 | 247.345 | [6 empty] | 0 |  | 0
2015-10-29 | 258.208 | [6 empty] | 0 |  | 0
2015-10-30 | 232.052 | [6 empty] | 0 |  | 0
2015-10-31 | 255.255 | [6 empty] | 0 |  | 0
2015-11-01 | 254.5015 | [6 empty] | 0 |  | 0
2015-11-02 | 254.5015 | 7 | 28 | 2 | 59 | 13 | 2.7 | 73 | 18 | 0 | 2015-11-11 | 2015-11-20
2015-11-03 | 145.149 | [6 empty] | 0 |  | 2
2015-11-04 | 223.966 | [6 empty] | 0 |  | 17
2015-11-05 | 495.164 | [6 empty] | 0 |  | 26
2015-11-06 | 362.468 | [6 empty] | 0 |  | 11
2015-11-07 | 249.189 | [6 empty] | 0 |  | 0
2015-11-08 | 686.691 | [6 empty] | 0 |  | 0
2015-11-09 | 686.691 | [6 empty] | 0 |  | 46
2015-11-10 | 444.549 | [6 empty] | 0 |  | 0
2015-11-11 | 380.492 | [6 empty] | 208 |  | 0
2015-11-12 | 316.363 | [6 empty] | 346 |  | 0
2015-11-13 | 298.503 | [6 empty] | 376 |  | 0
2015-11-14 | 348.339 | [6 empty] | 0 |  | 8
2015-11-15 | 872.881 | [6 empty] | 0 |  | 0
2015-11-16 | 872.881 | 5 | 216 | 2 | 12 | 13 | 2.7 | 0 |  | 47 | 2015-11-24 | 2015-12-04
2015-11-17 | 433.799 | [6 empty] | 0 |  | 0
2015-11-18 | 354.657 | [6 empty] | 0 |  | 0
2015-11-19 | 326.688 | [6 empty] | 0 |  | 0
2015-11-20 | 365.1 | [6 empty] | 0 |  | 0
2015-11-21 | 276.985 | [6 empty] | 0 |  | 0
2015-11-22 | 282.791 | [6 empty] | 0 |  | 0
2015-11-23 | 282.791 | [6 empty] | 0 |  | 0
2015-11-24 | 1347.686 | [6 empty] | 0 |  | 82
2015-11-25 | 699.991 | [6 empty] | 0 |  | 0
2015-11-26 | 467.122 | [6 empty] | 0 |  | 0
2015-11-27 | 400.836 | [6 empty] | 0 |  | 0
2015-11-28 | 367.445 | [6 empty] | 0 |  | 0
2015-11-29 | 974.031 | [6 empty] | 0 |  | 0
2015-11-30 | 974.031 | 2 | 10 | 2 | 16 | 1.5 | 3.4 | 0 | 60 | 86 | 2015-12-14 | 2015-12-23
2015-12-01 | 609.483 | [6 empty] | 421 |  | 0
2015-12-02 | 567.42 | [6 empty] | 0 |  | 7
2015-12-03 | 542.519 | [6 empty] | 0 |  | 7
2015-12-04 | 549.76 | [6 empty] | 0 |  | 0
2015-12-05 | 350.539 | [6 empty] | 0 |  | 3
2015-12-06 | 378.2685 | [6 empty] | 0 |  | 0
2015-12-07 | 378.2685 | [6 empty] | 0 |  | 0
2015-12-08 | 267.383 | [6 empty] | 0 |  | 0
2015-12-09 | 314.21 | [6 empty] | 0 |  | 0
2015-12-10 | 347.393 | [6 empty] | 0 |  | 11
2015-12-11 | 400.962 | [6 empty] | 0 |  | 0
2015-12-12 | 251.341 | [6 empty] | 0 |  | 3
2015-12-13 | 289.7075 | [6 empty] | 0 |  | 0
2015-12-14 | 289.7075 | [6 empty] | 0 |  | 0
2015-12-15 | 290.233 | [6 empty] | 0 |  | 0
2015-12-16 | 275.222 | [6 empty] | 0 |  | 4
2015-12-17 | 281.711 | [6 empty] | 0 |  | 2
2015-12-18 | 326.334 | [6 empty] | 0 |  | 0
2015-12-19 | 246.473 | [6 empty] | 0 |  | 0
2015-12-20 | 273.0335 | [6 empty] | 0 |  | 0
2015-12-21 | 273.0335 | [6 empty] | 0 |  | 0
2015-12-22 | 272.485 | [6 empty] | 0 |  | 0
2015-12-23 | 315.01 | [6 empty] | 187 |  | 0
2015-12-24 | 294.452 | [6 empty] | 114 |  | 0
2015-12-25 | 334.793 | [6 empty] | 0 |  | 0
2015-12-26 | 334.794 | [6 empty] | 0 |  | 9
2015-12-27 | 285.2775 | [6 empty] | 0 |  | 0
2015-12-28 | 285.2775 | [6 empty] | 0 |  | 0
2015-12-29 | 273.739 | [6 empty] | 69 |  | 0
2015-12-30 | 194.322 | [6 empty] | 151 |  | 10
2015-12-31 | 250.428 | [6 empty] | 69 |  | 0
2016-01-01 | 283.982 | [6 empty] | 0 |  | 0
2016-01-02 | 238.859 | [6 empty] | 0 |  | 0
2016-01-03 | 246.3095 | [6 empty] | 412 |  | 0
2016-01-04 | 246.3095 | 9 | 216 | 2 | 35 | 3 | 2.7 | 0 | 2 | 7 | 2016-01-11 | 2015-01-22
2016-01-05 | 265.136 | [6 empty] | 0 |  | 7
2016-01-06 | 361.084 | [6 empty] | 167 |  | 0
2016-01-07 | 388.006 | [6 empty] | 192 |  | 0
2016-01-08 | 201.671 | [6 empty] | 0 |  | 0
2016-01-09 | 277.998 | [6 empty] | 0 |  | 0
2016-01-10 | 237.8095 | [6 empty] | 0 |  | 0
2016-01-11 | 237.8095 | [6 empty] | 0 |  | 0
2016-01-12 | 242.236 | [6 empty] | 0 |  | 0
2016-01-13 | 313.339 | [6 empty] | 0 |  | 0
2016-01-14 | 227.525 | [6 empty] | 0 |  | 0
2016-01-15 | 218.956 | [6 empty] | 0 |  | 0
2016-01-16 | 266.377 | [6 empty] | 0 |  | 15
2016-01-17 | 239.5335 | [6 empty] | 0 |  | 0
2016-01-18 | 239.5335 | [6 empty] | 0 |  | 0
2016-01-19 | 243.81 | [6 empty] | 0 |  | 0
2016-01-20 | 236.901 | [6 empty] | 0 |  | 0
2016-01-21 | 238.006 | [6 empty] | 0 |  | 0
2016-01-22 | 228.672 | [6 empty] | 0 |  | 0
2016-01-23 | 240.187 | [6 empty] | 0 |  | 0
2016-01-24 | 222.495 | [6 empty] | 0 |  | 0
2016-01-25 | 222.495 | [6 empty] | 135 |  | 0
2016-01-26 | 219.326 | [6 empty] | 0 |  | 2
2016-01-27 | 233.226 | [6 empty] | 290 |  | 6
2016-01-28 | 234.779 | [6 empty] | 0 |  | 0
2016-01-29 | 264.869 | [6 empty] | 0 | 2 | 0 | 2016-02-07 | 2016-02-12
2016-01-30 | 219.55 | [6 empty] | 0 |  | 0
2016-01-31 | 219.551 | [6 empty] | 0 |  | 0
2016-02-01 | 347.319 | [6 empty] | 0 |  | 0
2016-02-02 | 287.774 | 6 | 1340 | 2 | 30 | 8 | 5.8 | 0 |  | 0 | 2016-02-12 | 2016-02-19
2016-02-03 | 287.033 | [6 empty] | 0 |  | 1
2016-02-04 | 278.361 | [6 empty] | 246 |  | 0
2016-02-05 | 268.025 | [6 empty] | 216 |  | 6
2016-02-06 | 337.082 | [6 empty] | 0 |  | 14
2016-02-07 | 327.861 | [6 empty] | 0 |  | 0
2016-02-08 | 327.861 | [6 empty] | 81 |  | 12
2016-02-09 | 339.905 | [6 empty] | 0 |  | 4
2016-02-10 | 193.558 | [6 empty] | 146 |  | 0
2016-02-11 | 331.201 | [6 empty] | 122 |  | 0
2016-02-12 | 229.082 | [6 empty] | 0 |  | 0
2016-02-13 | 230.79 | [6 empty] | 0 |  | 0
2016-02-14 | 269.3255 | [6 empty] | 0 |  | 0
2016-02-15 | 269.3255 | [6 empty] | 103 |  | 0
2016-02-16 | 246.967 | [6 empty] | 0 |  | 0
2016-02-17 | 252.568 | [6 empty] | 0 |  | 0
2016-02-18 | 248.312 | [6 empty] | 96 |  | 0
2016-02-19 | 232.691 | [6 empty] | 0 |  | 0
2016-02-20 | 257.939 | [6 empty] | 0 |  | 3
2016-02-21 | 229.0685 | [6 empty] | 0 |  | 0
2016-02-22 | 229.0685 | [6 empty] | 70 |  | 0
2016-02-23 | 233.064 | [6 empty] | 103 |  | 0
2016-02-24 | 248.629 | [6 empty] | 0 |  | 0
2016-02-25 | 228.701 | [6 empty] | 0 |  | 0
2016-02-26 | 241.086 | [6 empty] | 0 |  | 0
2016-02-27 | 248.517 | [6 empty] | 0 |  | 0
2016-02-28 | 243.7805 | [6 empty] | 0 |  | 0
2016-02-29 | 243.7805 | 12 | 2 | 2 | 80 | 5.2 | 2.1 | 0 | 1 | 10 | 2016-03-09 | 2016-03-18
2016-03-01 | 269.869 | [6 empty] | 0 |  | 12
2016-03-02 | 254.055 | [6 empty] | 0 |  | 5
2016-03-03 | 348.064 | [6 empty] | 0 |  | 18
2016-03-04 | 277.798 | [6 empty] | 0 |  | 0
2016-03-05 | 297.093 | [6 empty] | 0 |  | 0
2016-03-06 | 260.199 | [6 empty] | 0 |  | 0
2016-03-07 | 260.199 | [6 empty] | 0 |  | 8
2016-03-08 | 280.058 | [6 empty] | 0 |  | 8
2016-03-09 | 379.402 | [6 empty] | 0 |  | 12
2016-03-10 | 290.841 | [6 empty] | 0 |  | 0
2016-03-11 | 331.992 | [6 empty] | 0 |  | 0
2016-03-12 | 194.565 | [6 empty] | 0 |  | 0
2016-03-13 | 269.7695 | [6 empty] | 0 |  | 0
2016-03-14 | 269.7695 | [6 empty] | 0 |  | 5
2016-03-15 | 272.262 | [6 empty] | 0 |  | 3
2016-03-16 | 421.987 | [6 empty] | 0 |  | 25
2016-03-17 | 409.817 | [6 empty] | 0 |  | 0
2016-03-18 | 291.805 | [6 empty] | 0 |  | 0
2016-03-19 | 297.808 | [6 empty] | 0 |  | 0
2016-03-20 | 291.284 | [6 empty] | 0 |  | 0
2016-03-21 | 291.284 | [6 empty] | 0 |  | 0
2016-03-22 | 309.636 | [6 empty] | 0 |  | 8
2016-03-23 | 177.973 | [6 empty] | 0 |  | 0
2016-03-24 | 328.82 | [6 empty] | 0 |  | 0
2016-03-25 | 160.127 | [6 empty] | 0 | Not Tested | 0 | 2016-05-10 | N/A
2016-03-26 | 259.547 | [6 empty] | 0 |  | 0
2016-03-27 | 250 | [6 empty] | 0 |  | 0
2016-03-28 | 250 | [6 empty] | 0 |  | 0
2016-03-29 | 250 | 9 | 440 | 2 | 103 | 5 | 3.6 | 71 |  | 0 | 2016-04-07 | 2016-04-19
2016-03-30 | 250 | [6 empty] | 0 |  | 0
2016-03-31 | 250 | [6 empty] | 0 |  | 22
2016-04-01 | 250 | [6 empty] | 0 |  | 0
2016-04-02 | 250 | [6 empty] | 0 |  | 0
2016-04-03 | 250 | [6 empty] | 0 |  | 0
2016-04-04 | 250 | [6 empty] | 237 |  | 3
2016-04-05 | 250 | [6 empty] | 0 |  | 0
2016-04-06 | 250 | [6 empty] | 0 |  | 0
2016-04-07 | 256.859 | [6 empty] | 0 |  | 0
2016-04-08 | 321.097 | [6 empty] | 0 |  | 0
2016-04-09 | 228.271 | [6 empty] | 0 |  | 0
2016-04-10 | 248.048 | [6 empty] | 0 |  | 0
2016-04-11 | 248.048 | [6 empty] | 0 |  | 4
2016-04-12 | 247.265 | [6 empty] | 0 |  | 0
2016-04-13 | 342.747 | [6 empty] | 0 |  | 6
2016-04-14 | 342.847 | [6 empty] | 0 |  | 16
2016-04-15 | 357.259 | [6 empty] | 0 |  | 0
2016-04-16 | 354.386 | [6 empty] | 0 |  | 0
2016-04-17 | 273.8355 | [6 empty] | 0 |  | 0
2016-04-18 | 273.8355 | [6 empty] | 0 |  | 0
2016-04-19 | 269.043 | [6 empty] | 0 |  | 0
2016-04-20 | 266.458 | [6 empty] | 0 |  | 0
2016-04-21 | 255.136 | [6 empty] | 0 |  | 0
2016-04-22 | 316.936 | [6 empty] | 0 |  | 0
2016-04-23 | 224.572 | [6 empty] | 0 |  | 0
2016-04-24 | 270.842 | [6 empty] | 0 |  | 0
2016-04-25 | 270.842 | 8 | 230 | 2 | 56 | 3.8 | 3.2 | 0 |  | 6 | 2016-05-10 | 2016-05-20
2016-04-26 | 327.755 | [6 empty] | 0 |  | 6
2016-04-27 | 183.069 | [6 empty] | 0 |  | 3
2016-04-28 | 285.11 | [6 empty] | 0 |  | 7
2016-04-29 | 263.66 | [6 empty] | 0 |  | 0
2016-04-30 | 281.329 | [6 empty] | 0 |  | 0
2016-05-01 | 250.7305 | [6 empty] | 0 |  | 0
2016-05-02 | 250.7305 | [6 empty] | 0 |  | 0
2016-05-03 | 301.473 | [6 empty] | 0 |  | 10
2016-05-04 | 278.146 | [6 empty] | 0 |  | 0
2016-05-05 | 255.455 | [6 empty] | 0 |  | 0
2016-05-06 | 302.403 | [6 empty] | 0 |  | 0
2016-05-07 | 229.238 | [6 empty] | 0 |  | 0
2016-05-08 | 251.745 | [6 empty] | 0 |  | 0
2016-05-09 | 251.745 | [6 empty] | 0 |  | 0
2016-05-10 | 249.992 | [6 empty] | 0 | 2 | 0 | 2016-05-13 | 2016-05-20
2016-05-11 | 258.441 | [6 empty] | 0 |  | 0
2016-05-12 | 264.74 | [6 empty] | 0 |  | 0
2016-05-13 | 245.946 | [6 empty] | 0 |  | 0
2016-05-14 | 262.856 | [6 empty] | 0 |  | 0
2016-05-15 | 261.768 | [6 empty] | 0 |  | 0
2016-05-16 | 261.768 | [6 empty] | 0 |  | 0
2016-05-17 | 251.745 | [6 empty] | 0 |  | 0
2016-05-18 | 193.297 | [6 empty] | 145 |  | 0
2016-05-19 | 229.176 | [6 empty] | 0 |  | 0
2016-05-20 | 266.939 | [6 empty] | 0 |  | 0
2016-05-21 | 195.543 | [6 empty] | 0 |  | 0
2016-05-22 | 234.773 | [6 empty] | 0 |  | 0
2016-05-23 | 234.773 | 3 | 12 | 2 | 7 | 4.5 | 2.4 | 48 | 2 | 0 | 2016-05-30 | 2016-06-09
2016-05-24 | 257.256 | [6 empty] | 0 |  | 0
2016-05-25 | 245.798 | [6 empty] | 0 |  | 0
2016-05-26 | 180.971 | [6 empty] | 0 |  | 0
2016-05-27 | 229.549 | [6 empty] | 0 |  | 6
2016-05-28 | 202.468 | [6 empty] | 0 |  | 0
2016-05-29 | 244.0225 | [6 empty] | 0 |  | 0
2016-05-30 | 244.0225 | [6 empty] | 0 |  | 0
2016-05-31 | 222.935 | [6 empty] | 0 |  | 0
2016-06-01 | 193.799 | [6 empty] | 0 |  | 0
2016-06-02 | 238.212 | [6 empty] | 56 |  | 4
2016-06-03 | 225.318 | [6 empty] | 0 |  | 0
2016-06-04 | 579.353 | [6 empty] | 0 |  | 57
2016-06-05 | 1660.1115 | [6 empty] | 0 |  | 0
2016-06-06 | 1660.1115 | [6 empty] | 0 |  | 2.5
2016-06-07 | 38.12 | [6 empty] | 0 |  | 0
2016-06-08 | 1218.128 | [6 empty] | 0 |  | 0
2016-06-09 | 470.952 | [6 empty] | 0 |  | 0
2016-06-10 | 274.067 | [6 empty] | 0 |  | 0
2016-06-11 | 370.619 | [6 empty] | 0 |  | 0
2016-06-12 | 307.508 | [6 empty] | 0 |  | 0
2016-06-13 | 307.508 | [6 empty] | 0 |  | 3
2016-06-14 | 373.382 | [6 empty] | 0 |  | 10
2016-06-15 | 507.998 | [6 empty] | 0 |  | 5
2016-06-16 | 384.451 | [6 empty] | 0 |  | 0
2016-06-17 | 324.184 | [6 empty] | 0 |  | 0
2016-06-18 | 339.51 | [6 empty] | 0 |  | 0
2016-06-19 | 790.979 | [6 empty] | 0 |  | 0
2016-06-20 | 790.979 | 4 | 2400 | 2 | 8 | 10 | 2.5 | 60 | 2 | 42 | 2016-06-28 | 2016-07-08
2016-06-21 | 770.679 | [6 empty] | 0 |  | 0
2016-06-22 | 549.319 | [6 empty] | 0 |  | 0
2016-06-23 | 450.331 | [6 empty] | 0 |  | 0
2016-06-24 | 409.525 | [6 empty] | 0 |  | 0
2016-06-25 | 420.709 | [6 empty] | 0 |  | 0
2016-06-26 | 337.869 | [6 empty] | 0 |  | 0
2016-06-27 | 337.869 | [6 empty] | 0 |  | 3
2016-06-28 | 354.942 |  | 4 |  |  |  |  | 0 |  | 0 | 2016-07-05 | 2016-07-08
2016-06-29 | 341.692 | [6 empty] | 0 |  | 0
2016-06-30 | 348.339 | [6 empty] | 0 |  | 0
2016-07-01 | 358.178 | [6 empty] | 0 |  | 0
2016-07-02 | 288.689 | [6 empty] | 0 |  | 0
2016-07-03 | 306.813 | [6 empty] | 0 |  | 0
2016-07-04 | 306.813 | [6 empty] | 0 |  | 0
2016-07-05 | 329.203 | [6 empty] | 0 |  | 4
2016-07-06 | 312.863 | [6 empty] | 0 |  | 3
2016-07-07 | 313.081 | [6 empty] | 0 |  | 0
2016-07-08 | 302.342 | [6 empty] | 0 |  | 0
2016-07-09 | 343.333 | [6 empty] | 0 |  | 2
2016-07-10 | 271.5275 | [6 empty] | 0 |  | 0
2016-07-11 | 271.5275 | [6 empty] | 0 |  | 0
2016-07-12 | 286.039 | [6 empty] | 0 |  | 0
2016-07-13 | 359.205 | [6 empty] | 0 |  | 0
2016-07-14 | 186.53 | [6 empty] | 0 |  | 0
2016-07-15 | 318.469 | [6 empty] | 0 |  | 0
2016-07-16 | 270.455 | [6 empty] | 0 |  | 0
2016-07-17 | 315.0795 | [6 empty] | 0 |  | 0
2016-07-18 | 315.0795 | 3 | 38 | 2 | 4 | 10 | 2.9 | 0 |  | 15 | 2016-07-25 | 2016-08-03
2016-07-19 | 212.866 | [6 empty] | 0 |  | 0
2016-07-20 | 317.66 | [6 empty] | 0 |  | 0
2016-07-21 | 292.636 | [6 empty] | 0 |  | 0
2016-07-22 | 294.044 | [6 empty] | 0 |  | 0
2016-07-23 | 337.787 | [6 empty] | 0 |  | 0
2016-07-24 | 282.582 | [6 empty] | 0 |  | 0
2016-07-25 | 282.582 | [6 empty] | 0 |  | 0
2016-07-26 | 280.818 | [6 empty] | 0 |  | 0
2016-07-27 | 281.657 | [6 empty] | 0 |  | 0
2016-07-28 | 274.446 | [6 empty] | 0 |  | 0
2016-07-29 | 326.253 | [6 empty] | 0 |  | 0
2016-07-30 | 234.609 | [6 empty] | 0 |  | 0
2016-07-31 | 285.5705 | [6 empty] | 0 |  | 0
2016-08-01 | 285.5705 | [6 empty] | 0 |  | 0
2016-08-02 | 263.905 | [6 empty] | 0 |  | 0
2016-08-03 | 266.312 | [6 empty] | 0 |  | 4
2016-08-04 | 982.045 | [6 empty] | 0 |  | 90
2016-08-05 | 1397.382 | [6 empty] | 0 |  | 10
2016-08-06 | 939.556 | [6 empty] | 0 |  | 3
2016-08-07 | 523.3325 | [6 empty] | 0 |  | 0
2016-08-08 | 523.3325 | [6 empty] | 0 |  | 2
2016-08-09 | 480.289 | [6 empty] | 0 |  | 0
2016-08-10 | 442.575 | [6 empty] | 0 |  | 0
2016-08-11 | 406.921 | [6 empty] | 0 |  | 0
2016-08-12 | 471.903 | [6 empty] | 0 |  | 0
2016-08-13 | 308.952 | [6 empty] | 0 |  | 0
2016-08-14 | 356.881 | [6 empty] | 0 |  | 0
2016-08-15 | 356.881 | 2 | 16 | 2 | 10 | 12 | 2.8 | 0 |  | 0 | 2016-08-24 | 2016-09-01
2016-08-16 | 467.543 | [6 empty] | 0 |  | 1
2016-08-17 | 346.904 | [6 empty] | 0 |  | 0
2016-08-18 | 346.904 | [6 empty] | 0 |  | 0
2016-08-19 | 289.665 | [6 empty] | 0 |  | 0
2016-08-20 | 297.269 | [6 empty] | 0 |  | 0
2016-08-21 | 306.569 | [6 empty] | 0 |  | 0
2016-08-22 | 306.569 | [6 empty] | 0 |  | 0
2016-08-23 | 361.285 | [6 empty] | 0 |  | 14
2016-08-24 | 1286.5295 | [6 empty] | 0 |  | 40
2016-08-25 | 1286.5295 | [6 empty] | 0 |  | 35
2016-08-26 | 1019.945 | [6 empty] | 0 |  | 0
2016-08-27 | 471.524 | [6 empty] | 0 |  | 0
2016-08-28 | 479.203 | [6 empty] | 0 |  | 0
2016-08-29 | 479.203 | [6 empty] | 0 |  | 0
2016-08-30 | 429.993 | [6 empty] | 0 |  | 0
2016-08-31 | 410.903 | [6 empty] | 0 |  | 0
MINIMUM | 38.12 | 2 | 2 | 2 | 4 | 1.5 | 2.1 | 0 | 1 | 0
AVERAGE | 330.1054 | 5.4615 | 389.2308 | 2 | 30 | 7.5385 | 3.1346 | 25.5 | 1.8571 | 2.9904
MAXIMUM | 1660.1115 | 12 | 2400 | 2 | 103 | 13 | 5.8 | 376 | 2 | 90
| 120488.463 | [6 empty] | 7176 |  | 1094.5
| SAMPLE COUNT | 14

## 16-17
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 16/17
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Date analysis results obtained | Date Published
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2016-09-01 | 388.12 | [6 empty] | 0 |  | 0
2016-09-02 | 370.782 | [6 empty] | 0 |  | 0
2016-09-03 | 405.445 | [6 empty] | 0 |  | 9
2016-09-04 | 328.4585 | [6 empty] | 0 |  | 0
2016-09-05 | 328.4585 | [6 empty] | 90 |  | 0
2016-09-06 | 336.836 | [6 empty] | 0 |  | 0
2016-09-07 | 450.23 | [6 empty] | 0 |  | 0
2016-09-08 | 273.301 | [6 empty] | 0 |  | 0
2016-09-09 | 318.446 | [6 empty] | 0 |  | 0
2016-09-10 | 259.786 | [6 empty] | 0 |  | 2
2016-09-11 | 320.3795 | [6 empty] | 0 |  | 0
2016-09-12 | 320.3795 | 5 | 16 | 2 | 15 | 7.6 | 2.6 | 31 |  | 0 | 2016-09-22 | 2016-10-06
2016-09-13 | 329.758 | [6 empty] | 0 |  | 0
2016-09-14 | 300.737 | [6 empty] | 0 |  | 0
2016-09-15 | 311.496 | [6 empty] | 0 |  | 4
2016-09-16 | 251.95 | [6 empty] | 0 |  | 7
2016-09-17 | 349.924 | [6 empty] | 0 |  | 0
2016-09-18 | 293.3475 | [6 empty] | 0 |  | 0
2016-09-19 | 293.3475 | [6 empty] | 76 |  | 0
2016-09-20 | 310.365 | [6 empty] | 0 | 2 | 0 | 2016-10-04 | 2016-10-06
2016-09-21 | 307.541 | [6 empty] | 0 |  | 4
2016-09-22 | 322.129 | [6 empty] | 92 |  | 5
2016-09-23 | 359.529 | [6 empty] | 0 |  | 0
2016-09-24 | 240.502 | [6 empty] | 0 |  | 0
2016-09-25 | 291.469 | [6 empty] | 0 |  | 0
2016-09-26 | 291.469 | [6 empty] | 0 |  | 6
2016-09-27 | 360.809 | [6 empty] | 0 |  | 0
2016-09-28 | 278.801 | [6 empty] | 0 |  | 0
2016-09-29 | 265.995 | [6 empty] | 0 |  | 0
2016-09-30 | 301.579 | [6 empty] | 0 |  | 0
2016-10-01 | 244.639 | [6 empty] | 0 |  | 0
2016-10-02 | 348.712 | [6 empty] | 0 |  | 0
2016-10-03 | 346.0473 | [6 empty] | 0 |  | 0
2016-10-04 | 358.654 | [6 empty] | 0 |  | 8
2016-10-05 | 282.459 | [6 empty] | 0 |  | 0
2016-10-06 | 286.636 | [6 empty] | 0 |  | 0
2016-10-07 | 334.467 | [6 empty] | 0 |  | 0
2016-10-08 | 236.611 | [6 empty] | 67 |  | 0
2016-10-09 | 266.0265 | [6 empty] | 0 |  | 0
2016-10-10 | 266.0265 | 5 | 50 | 2 | 13 | 5.7 | 2 | 0 | 2 | 0 | 2016-10-17 | 2016-10-28
2016-10-11 | 62.706 | [6 empty] | 220 |  | 5
2016-10-12 | 267.784 | [6 empty] | 58 |  | 0
2016-10-13 | 259.23 | [6 empty] | 0 |  | 0
2016-10-14 | 430.905 | [6 empty] | 0 |  | 0
2016-10-15 | 234.094 | [6 empty] | 0 |  | 0
2016-10-16 | 404.945 | [6 empty] | 0 |  | 0
2016-10-17 | 341.0783 | [6 empty] | 177 |  | 0
2016-10-18 | 393.0413 | [6 empty] | 0 |  | 0
2016-10-19 | 389.983 | [6 empty] | 198 |  | 0
2016-10-20 | 177.849 | [6 empty] | 211 |  | 0
2016-10-21 | 385.046 | [6 empty] | 0 |  | 0
2016-10-22 | 151.47 | [6 empty] | 0 |  | 0
2016-10-23 | 252.0405 | [6 empty] | 0 |  | 0
2016-10-24 | 252.0405 | [6 empty] | 104 |  | 2
2016-10-25 | 328.464 | [6 empty] | 0 |  | 0
2016-10-26 | 204.326 | [6 empty] | 147 |  | 0
2016-10-27 | 259.571 | [6 empty] | 151 |  | 0
2016-10-28 | 337.079 | [6 empty] | 90 |  | 0
2016-10-29 | 239.616 | [6 empty] | 70 |  | 7
2016-10-30 | 291.177 | [6 empty] | 0 |  | 0
2016-10-31 | 291.177 | [6 empty] | 116 |  | 0
2016-11-01 | 176.189 | [6 empty] | 0 |  | 0
2016-11-02 | 281.657 | [6 empty] | 169 |  | 0
2016-11-03 | 265.344 | [6 empty] | 141 |  | 0
2016-11-04 | 322.337 | [6 empty] | 0 |  | 0
2016-11-05 | 236.121 | [6 empty] | 0 |  | 0
2016-11-06 | 251.672 | [6 empty] | 0 |  | 0
2016-11-07 | 251.672 | 13 | <2 | <2 | 30 | 2.9 | 1.1 | 0 |  | 0 | 2016-11-15 | 2016-11-28
2016-11-08 | 311.69 | [6 empty] | 0 |  | 0
2016-11-09 | 254.582 | [6 empty] | 125 |  | 0
2016-11-10 | 86.634 | [6 empty] | 0 |  | 38
2016-11-11 | 251.819 | [6 empty] | 0 |  | 0
2016-11-12 | 308.6 | [6 empty] | 0 |  | 0
2016-11-13 | 303.2465 | [6 empty] | 0 |  | 0
2016-11-14 | 303.2465 | [6 empty] | 0 |  | 0
2016-11-15 | 181.666 | [6 empty] | 0 |  | 0
2016-11-16 | 308.571 | [6 empty] | 0 |  | 0
2016-11-17 | 207.279 | [6 empty] | 0 |  | 0
2016-11-18 | 310.253 | [6 empty] | 0 |  | 0
2016-11-19 | 212.17 | [6 empty] | 0 |  | 0
2016-11-20 | 256.7165 | [6 empty] | 0 |  | 0
2016-11-21 | 256.7165 | [6 empty] | 0 | 2 | 0 | 2016-11-29 | 2016-12-08
2016-11-22 | 248.562 | [6 empty] | 0 |  | 0
2016-11-23 | 240.2845 | [6 empty] | 0 |  | 0
2016-11-24 | 240.2845 | [6 empty] | 0 |  | 0
2016-11-25 | 315.932 | [6 empty] | 0 |  | 0
2016-11-26 | 192.34 | [6 empty] | 0 |  | 0
2016-11-27 | 293.197 | [6 empty] | 0 |  | 0
2016-11-28 | 293.197 | [6 empty] | 0 |  | 0
2016-11-29 | 188.606 | [6 empty] | 0 |  | 0
2016-11-30 | 303.763 | [6 empty] | 0 |  | 0
2016-12-01 | 234.925 | [6 empty] | 0 |  | 0
2016-12-02 | 197.451 | [6 empty] | 0 |  | 0
2016-12-03 | 247.054 | [6 empty] | 0 |  | 0
2016-12-04 | 257.754 | [6 empty] | 0 |  | 0
2016-12-05 | 257.754 | 11 | <2 | <2 | 25 | 2.2 | 0.74 | 0 | 1 | 12 | 2016-12-13 | 2016-12-23
2016-12-06 | 219.114 | [6 empty] | 0 |  | 58
2016-12-07 | 141.5385 | [6 empty] | 0 |  | 3
2016-12-08 | 141.5385 | [6 empty] | 0 |  | 11
2016-12-09 | 351.752 | [6 empty] | 0 |  | 10
2016-12-10 | 319.196 | [6 empty] | 0 |  | 0
2016-12-11 | 242.89 | [6 empty] | 0 |  | 0
2016-12-12 | 242.89 | [6 empty] | 0 |  | 0
2016-12-13 | 253.028 | [6 empty] | 0 |  | 0
2016-12-14 | 251.842 | [6 empty] | 0 |  | 0
2016-12-15 | 250.296 | [6 empty] | 0 |  | 0
2016-12-16 | 307.043 | [6 empty] | 0 |  | 0
2016-12-17 | 221.734 | [6 empty] | 0 |  | 0
2016-12-18 | 290.2505 | [6 empty] | 0 |  | 0
2016-12-19 | 290.2505 | [6 empty] | 0 |  | 0
2016-12-20 | 296.4 | [6 empty] | 0 |  | 0
2016-12-21 | 221.711 | [6 empty] | 63 |  | 0
2016-12-22 | 305.174 | [6 empty] | 99 |  | 0
2016-12-23 | 280.706 | [6 empty] | 82 |  | 13
2016-12-24 | 240.662 | [6 empty] | 0 |  | 0
2016-12-25 | 292.939 | [6 empty] | 0 |  | 0
2016-12-26 | 292.939 | [6 empty] | 0 |  | 0
2016-12-27 | 291.214 | [6 empty] | 51 |  | 3
2016-12-28 | 295.473 | [6 empty] | 99 |  | 0
2016-12-29 | 256.29 | [6 empty] | 48 |  | 0
2016-12-30 | 251.804 | [6 empty] | 0 |  | 0
2016-12-31 | 247.758 | [6 empty] | 65 |  | 0
2017-01-01 | 286.615 | [6 empty] | 0 |  | 0
2017-01-02 | 286.615 | [6 empty] | 65 |  | 0
2017-01-03 | 1083.19 | [6 empty] | 92 |  | 95
2017-01-04 | 468.395 | 9 | 5 | <2 | 39 | 4.4 | 0.84 | 71 |  | 0 | 2017-01-10 | 2017-01-20
2017-01-05 | 294.09 | [6 empty] | 215 | 1 | 0 | 2017-01-16 | 2017-01-20
2017-01-06 | 605.813 | [6 empty] | 202 |  | 21
2017-01-07 | 657.199 | [6 empty] | 69 |  | 19
2017-01-08 | 449.355 | [6 empty] | 0 |  | 0
2017-01-09 | 449.355 | [6 empty] | 77 |  | 8
2017-01-10 | 339.151 | [6 empty] | 0 |  | 0
2017-01-11 | 322.252 | [6 empty] | 116 |  | 0
2017-01-12 | 300.407 | [6 empty] | 0 |  | 22
2017-01-13 | 487.775 | [6 empty] | 0 |  | 3
2017-01-14 | 300.475 | [6 empty] | 0 |  | 0
2017-01-15 | 329.483 | [6 empty] | 0 |  | 0
2017-01-16 | 329.483 | [6 empty] | 0 |  | 8
2017-01-17 | 314.603 | [6 empty] | 0 |  | 0
2017-01-18 | 364.294 | [6 empty] | 104 |  | 0
2017-01-19 | 245.751 | [6 empty] | 0 |  | 0
2017-01-20 | 258.832 | [6 empty] | 0 |  | 0
2017-01-21 | 301.265 | [6 empty] | 0 |  | 0
2017-01-22 | 543.166 | [6 empty] | 0 |  | 25
2017-01-23 | 271.522 | [6 empty] | 0 |  | 0
2017-01-24 | 287.047 | [6 empty] | 0 |  | 0
2017-01-25 | 319.304 | [6 empty] | 0 |  | 0
2017-01-26 | 227.718 | [6 empty] | 0 |  | 0
2017-01-27 | 426.007 | [6 empty] | 0 |  | 0
2017-01-28 | 253.367 | [6 empty] | 0 |  | 0
2017-01-29 | 279.8905 | [6 empty] | 0 |  | 0
2017-01-30 | 279.8905 | [6 empty] | 384 |  | 0
2017-01-31 | 290.971 | 12 | 2 | <2 | 40 | 4.1 | 0.9 | 88 | 1 | 0 | 2017-02-08 | 2017-02-22
2017-02-01 | 369.993 | [6 empty] | 0 |  | 0
2017-02-02 | 177.239 | [6 empty] | 0 |  | 0
2017-02-03 | 265.834 | [6 empty] | 0 |  | 0
2017-02-04 | 315.102 | [6 empty] | 0 |  | 0
2017-02-05 | 253.2085 | [6 empty] | 0 |  | 0
2017-02-06 | 253.2085 | [6 empty] | 175 |  | 0
2017-02-07 | 267.205 | [6 empty] | 159 |  | 0
2017-02-08 | 307.501 | [6 empty] | 208 |  | 0
2017-02-09 | 228.32 | [6 empty] | 0 |  | 4
2017-02-10 | 330.505 | [6 empty] | 0 |  | 0
2017-02-11 | 224.933 | [6 empty] | 0 |  | 0
2017-02-12 | 260.072 | [6 empty] | 0 |  | 0
2017-02-13 | 260.072 | [6 empty] | 418 |  | 0
2017-02-14 | 260.149 | [6 empty] | 116 |  | 2
2017-02-15 | 274.106 | [6 empty] | 109 |  | 0
2017-02-16 | 238.517 | [6 empty] | 0 |  | 0
2017-02-17 | 261.481 | [6 empty] | 119 |  | 0
2017-02-18 | 285.473 | [6 empty] | 0 |  | 0
2017-02-19 | 233.414 | [6 empty] | 0 |  | 4
2017-02-20 | 233.414 | [6 empty] | 184 |  | 0
2017-02-21 | 253.815 | [6 empty] | 281 |  | 6
2017-02-22 | 240.254 | [6 empty] | 216 |  | 3
2017-02-23 | 254.675 | [6 empty] | 222 |  | 0
2017-02-24 | 294.723 | [6 empty] | 49 |  | 0
2017-02-25 | 204.672 | [6 empty] | 0 |  | 0
2017-02-26 | 237.1005 | [6 empty] | 0 |  | 0
2017-02-27 | 237.1005 | 8 | 2420 | <2 | 15 | 4.1 | 1.4 | 100 | <1 | 9 | 2017-03-06 | 2017-03-17
2017-02-28 | 1266.706 | [6 empty] | 0 |  | 118
2017-03-01 | 1472.672 | [6 empty] | 0 |  | 18
2017-03-02 | 710.837 | [6 empty] | 0 |  | 2
2017-03-03 | 455.319 | [6 empty] | 0 |  | 0
2017-03-04 | 442.333 | [6 empty] | 0 |  | 0
2017-03-05 | 335.139 | [6 empty] | 0 |  | 0
2017-03-06 | 335.139 | [6 empty] | 119 |  | 8
2017-03-07 | 338.729 | [6 empty] | 112 |  | 0
2017-03-08 | 307.898 | [6 empty] | 130 |  | 0
2017-03-09 | 289.111 | [6 empty] | 0 |  | 0
2017-03-10 | 368.336 | [6 empty] | 0 |  | 0
2017-03-11 | 225.343 | [6 empty] | 0 |  | 0
2017-03-12 | 282.8975 | [6 empty] | 0 |  | 0
2017-03-13 | 282.8975 | [6 empty] | 0 |  | 0
2017-03-14 | 317.81 | [6 empty] | 0 |  | 15
2017-03-15 | 1484.483 | [6 empty] | 0 |  | 75
2017-03-16 | 2578.965 | [6 empty] | 0 |  | 89
2017-03-17 | 1007.902 | [6 empty] | 0 |  | 0
2017-03-18 | 1205.556 | [6 empty] | 0 |  | 40
2017-03-19 | 1953.031 | [6 empty] | 0 |  | 0
2017-03-20 | 1953.031 | [6 empty] | 0 |  | 246
2017-03-21 | 2029.969 | [6 empty] | 0 |  | 14
2017-03-22 | 1644.537 | [6 empty] | 0 |  | 2
2017-03-23 | 1232.399 | [6 empty] | 0 |  | 0
2017-03-24 | 960.86 | [6 empty] | 0 |  | 0
2017-03-25 | 801.562 | [6 empty] | 0 |  | 9
2017-03-26 | 721.6895 | [6 empty] | 0 |  | 0
2017-03-27 | 721.6895 | [6 empty] | 0 |  | 0
2017-03-28 | 591.14 | 9 | 66 | <2 | 21 | 5.1 | 3 | 0 | 133 | 0 | 2017-04-04 | 2017-05-03
2017-03-29 | 520.779 | [6 empty] | 0 |  | 0
2017-03-30 | 635.832 | [6 empty] | 0 |  | 32
2017-03-31 | 2200.885 | [6 empty] | 0 |  | 275
2017-04-01 | 2155.51 | [6 empty] | 0 |  | 0
2017-04-02 | 2082.6445 | [6 empty] | 0 |  | 0
2017-04-03 | 2082.6445 | [6 empty] | 0 |  | 0
2017-04-04 | 2116.265 | [6 empty] | 0 |  | 10
2017-04-05 | 1834.515 | [6 empty] | 0 |  | 13
2017-04-06 | 2153.389 | [6 empty] | 0 |  | 18
2017-04-07 | 1902.012 | [6 empty] | 0 |  | 25
2017-04-08 | 1010.405 | [6 empty] | 0 |  | 0
2017-04-09 | 846.507 | [6 empty] | 0 |  | 0
2017-04-10 | 846.507 | [6 empty] | 0 |  | 0
2017-04-11 | 632.344 | [6 empty] | 0 |  | 0
2017-04-12 | 531.378 | [6 empty] | 0 |  | 0
2017-04-13 | 514.972 | [6 empty] | 0 |  | 0
2017-04-14 | 486.887 | [6 empty] | 0 |  | 0
2017-04-15 | 521.086 | [6 empty] | 0 |  | 0
2017-04-16 | 397.755 | [6 empty] | 0 |  | 0
2017-04-17 | 397.755 | [6 empty] | 0 |  | 0
2017-04-18 | 497.089 | [6 empty] | 0 |  | 0
2017-04-19 | 344.788 | [6 empty] | 0 |  | 0
2017-04-20 | 478.352 | [6 empty] | 0 |  | 7
2017-04-21 | 331.894 | [6 empty] | 0 |  | 3
2017-04-22 | 329.556 | [6 empty] | 0 |  | 0
2017-04-23 | 396.59 | [6 empty] | 0 |  | 0
2017-04-24 | 396.59 | 5 | 9 | <2 | 10 | 3 | 2.5 | 0 | 1 | 3 | 2017-04-26 | 2017-05-03
2017-04-25 | 300.05 | [6 empty] | 0 |  | 0
2017-04-26 | 329.721 | [6 empty] | 0 |  | 0
2017-04-27 | 347.814 | [6 empty] | 0 |  | 4
2017-04-28 | 346.866 | [6 empty] | 0 |  | 0
2017-04-29 | 351.58 | [6 empty] | 0 |  | 0
2017-04-30 | 328.83 | [6 empty] | 0 |  | 0
2017-05-01 | 328.83 | [6 empty] | 0 |  | 0
2017-05-02 | 323.13 | [6 empty] | 0 |  | 0
2017-05-03 | 329.73 | [6 empty] | 0 |  | 0
2017-05-04 | 303.94 | [6 empty] | 0 |  | 0
2017-05-05 | 362.24 | [6 empty] | 0 |  | 2
2017-05-06 | 312.26 | [6 empty] | 0 |  | 5
2017-05-07 | 361.78 | [6 empty] | 0 |  | 0
2017-05-08 | 361.78 | [6 empty] | 0 |  | 1
2017-05-09 | 200.41 | [6 empty] | 0 |  | 3
2017-05-10 | 306.58 | [6 empty] | 0 |  | 3
2017-05-11 | 319.75 | [6 empty] | 0 |  | 5
2017-05-12 | 322.97 | [6 empty] | 0 |  | 0
2017-05-13 | 351.56 | [6 empty] | 0 |  | 5
2017-05-14 | 386.73 | [6 empty] | 0 |  | 0
2017-05-15 | 386.73 | [6 empty] | 0 |  | 17
2017-05-16 | 384.01 | [6 empty] | 0 |  | 0
2017-05-17 | 333.09 | [6 empty] | 0 |  | 0
2017-05-18 | 332.2 | [6 empty] | 0 |  | 0
2017-05-19 | 355.3 | [6 empty] | 0 |  | 2
2017-05-20 | 423.14 | [6 empty] | 0 |  | 13
2017-05-21 | 386.59 | [6 empty] | 0 |  | 0
2017-05-22 | 386.59 | 5 | 15 | <2 | 10 | 6.2 | 3.2 | 0 | <1 | 0 | 2017-05-23 | 2017-05-29
2017-05-23 | 346.35 | [6 empty] | 0 |  | 0
2017-05-24 | 339.095 | [6 empty] | 0 |  | 0
2017-05-25 | 311.602 | [6 empty] | 0 |  | 0
2017-05-26 | 323.853 | [6 empty] | 0 |  | 0
2017-05-27 | 363.902 | [6 empty] | 0 |  | 0
2017-05-28 | 286.737 | [6 empty] | 0 |  | 0
2017-05-29 | 286.737 | [6 empty] | 0 |  | 0
2017-05-30 | 373.179 | [6 empty] | 0 |  | 2
2017-05-31 | 308.272 | [6 empty] | 0 |  | 0
2017-06-01 | 310.811 | [6 empty] | 0 |  | 2
2017-06-02 | 236.073 | [6 empty] | 0 |  | 0
2017-06-03 | 246.374 | [6 empty] | 0 |  | 0
2017-06-04 | 292.383 | [6 empty] | 0 |  | 0
2017-06-05 | 292.383 | [6 empty] | 0 |  | 0
2017-06-06 | 282.206 | [6 empty] | 0 |  | 0
2017-06-07 | 275.536 | [6 empty] | 0 |  | 0
2017-06-08 | 279.564 | [6 empty] | 0 |  | 0
2017-06-09 | 296.273 | [6 empty] | 0 |  | 0
2017-06-10 | 547.258 | [6 empty] | 0 |  | 29
2017-06-11 | 1892.5735 | [6 empty] | 0 |  | 0
2017-06-12 | 1892.5735 | [6 empty] | 0 |  | 240
2017-06-13 | 2162.636 | [6 empty] | 0 |  | 100
2017-06-14 | 1937.782 | [6 empty] | 0 |  | 5
2017-06-15 | 1206.083 | [6 empty] | 0 |  | 0
2017-06-16 | 954.916 | [6 empty] | 0 |  | 0
2017-06-17 | 885.902 | [6 empty] | 0 |  | 19
2017-06-18 | 1271.3415 | [6 empty] | 0 |  | 0
2017-06-19 | 1271.3415 | 2 | 20 | 1 | 5 | 7.6 | 2.3 | 0 | <1 | 10 | 2017-06-20 | 2017-06-27
2017-06-20 | 781.766 | [6 empty] | 0 |  | 6
2017-06-21 | 752.722 | [6 empty] | 0 |  | 2
2017-06-22 | 626.564 | [6 empty] | 0 |  | 0
2017-06-23 | 683.967 | [6 empty] | 0 |  | 0
2017-06-24 | 413.056 | [6 empty] | 0 |  | 0
2017-06-25 | 454.223 | [6 empty] | 0 |  | 0
2017-06-26 | 454.223 | [6 empty] | 0 |  | 0
2017-06-27 | 402.686 | [6 empty] | 0 |  | 0
2017-06-28 | 366.516 | [6 empty] | 0 |  | 0
2017-06-29 | 344.275 | [6 empty] | 0 |  | 0
2017-06-30 | 416.451 | [6 empty] | 0 |  | 0
2017-07-01 | 383.769 | [6 empty] | 0 |  | 0
2017-07-02 | 277.5885 | [6 empty] | 0 |  | 0
2017-07-03 | 277.5885 | [6 empty] | 0 |  | 0
2017-07-04 | 555.176 | [6 empty] | 0 |  | 0
2017-07-05 | 389.785 | [6 empty] | 0 |  | 0
2017-07-06 | 284.334 | [6 empty] | 0 |  | 0
2017-07-07 | 328.026 | [6 empty] | 0 |  | 0
2017-07-08 | 400.571 | [6 empty] | 0 |  | 0
2017-07-09 | 379.3005 | [6 empty] | 0 |  | 0
2017-07-10 | 379.3005 | [6 empty] | 0 |  | 0
2017-07-11 | 484.081 | [6 empty] | 0 |  | 0
2017-07-12 | 328.994 | [6 empty] | 0 |  | 0
2017-07-13 | 367.772 | [6 empty] | 0 |  | 0
2017-07-14 | 270.538 | [6 empty] | 0 |  | 0
2017-07-15 | 322.913 | [6 empty] | 0 |  | 0
2017-07-16 | 367.3285 | [6 empty] | 0 |  | 0
2017-07-17 | 367.3285 | 6 | 13 | 1 | 14 | 7.1 | 2.4 | 0 | 10 | 11 | 2017-07-18 | 2017-07-25
2017-07-18 | 363.211 | [6 empty] | 0 |  | 0
2017-07-19 | 333.99 | [6 empty] | 0 |  | 0
2017-07-20 | 344.425 | [6 empty] | 0 |  | 0
2017-07-21 | 323.105 | [6 empty] | 0 |  | 0
2017-07-22 | 348.857 | [6 empty] | 0 |  | 0
2017-07-23 | 307.2275 | [6 empty] | 0 |  | 0
2017-07-24 | 307.2275 | [6 empty] | 0 |  | 0
2017-07-25 | 420.196 | [6 empty] | 0 |  | 0
2017-07-26 | 189.413 | [6 empty] | 0 |  | 0
2017-07-27 | 298.477 | [6 empty] | 0 |  | 0
2017-07-28 | 356.412 | [6 empty] | 0 |  | 0
2017-07-29 | 246.74 | [6 empty] | 0 |  | 0
2017-07-30 | 300.044 | [6 empty] | 0 |  | 0
2017-07-31 | 300.044 | [6 empty] | 0 |  | 0
2017-08-01 | 398.138 | [6 empty] | 0 |  | 0
2017-08-02 | 198.528 | [6 empty] | 0 |  | 0
2017-08-03 | 287.584 | [6 empty] | 0 |  | 0
2017-08-04 | 287.349 | [6 empty] | 0 |  | 0
2017-08-05 | 328.639 | [6 empty] | 0 |  | 0
2017-08-06 | 265.4445 | [6 empty] | 0 |  | 0
2017-08-07 | 265.4445 | [6 empty] | 0 |  | 0
2017-08-08 | 271.302 | [6 empty] | 0 |  | 0
2017-08-09 | 300.173 | [6 empty] | 0 |  | 0
2017-08-10 | 300.173 | [6 empty] | 0 |  | 0
2017-08-11 | 269.473 | [6 empty] | 0 |  | 0
2017-08-12 | 214.157 | [6 empty] | 0 |  | 0
2017-08-13 | 286.244 | [6 empty] | 0 |  | 0
2017-08-14 | 286.244 | 2 | 13 | 1 | 4 | 6.4 | 2.7 | 337 | <1 | 0 | 2017-08-15 | 2017-08-21
2017-08-15 | 351.808 | [6 empty] | 0 |  | 0
2017-08-16 | 182.257 | [6 empty] | 0 |  | 0
2017-08-17 | 260.698 | [6 empty] | 0 |  | 0
2017-08-18 | 273.701 | [6 empty] | 0 |  | 0
2017-08-19 | 273.701 | [6 empty] | 0 |  | 0
2017-08-20 | 240.4045 | [6 empty] | 0 |  | 0
2017-08-21 | 240.4045 | [6 empty] | 0 |  | 0
2017-08-22 | 256.186 | [6 empty] | 0 |  | 0
2017-08-23 | 259.547 | [6 empty] | 169 |  | 0
2017-08-24 | 270.692 | [6 empty] | 0 |  | 0
2017-08-25 | 256.4445 | [6 empty] | 0 |  | 5
2017-08-26 | 256.4445 | [6 empty] | 0 |  | 0
2017-08-27 | 260.736 | [6 empty] | 0 |  | 0
2017-08-28 | 260.736 | [6 empty] | 167 |  | 0
2017-08-29 | 238.529 | [6 empty] | 0 |  | 0
2017-08-30 | 255.93 | [6 empty] | 0 |  | 0
2017-08-31 | 305.574 | [6 empty] | 0 |  | 0
MINIMUM | 62.706 | 2 | 2 | 1 | 5 | 2.2 | 0.74 | 0 | 1 | 0
AVERAGE | 437.014 | 7.7778 | 361.1429 | 1.6667 | 21.3333 | 4.9778 | 1.6756 | 0 | 1.5 | 5.3397
MAXIMUM | 2578.965 | 13 | 2420 | 2 | 40 | 7.6 | 3.2 | 0 | 2 | 275
[8 empty] | 7713 |  | 1949
| SAMPLE COUNT | 13

## 17-18
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 17/18
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2017-09-01 | 210.78 | [8 empty] | 0
2017-09-02 | 282.37 | [6 empty] | 0 |  | 0
2017-09-03 | 237.282 | [6 empty] | 0 |  | 0
2017-09-04 | 237.282 | [6 empty] | 96/0.18 |  | 0
2017-09-05 | 257.58 | [6 empty] | 0 |  | 0
2017-09-06 | 259.742 | [6 empty] | 0 |  | 0
2017-09-07 | 250.084 | [6 empty] | 0 |  | 0
2017-09-08 | 288.517 | [6 empty] | 0 |  | 0
2017-09-09 | 185.281 | [6 empty] | 0 |  | 0
2017-09-10 | 267.5415 | [6 empty] | 0 |  | 0
2017-09-11 | 267.5415 | 2 | 20 | 1 | 10 | 5.9 | 3.4 | 61 | 1 | 0 | 9.30am | 2017-09-11 | 2017-09-26
2017-09-12 | 255.134 | [6 empty] | 0 |  | 0
2017-09-13 | 241.081 | [6 empty] | 277 |  | 0
2017-09-14 | 233.315 | [6 empty] | 0 |  | 0
2017-09-15 | 194.521 | [6 empty] | 75 |  | 0
2017-09-16 | 274.355 | [6 empty] | 0 |  | 0
2017-09-17 | 215.5125 | [6 empty] | 0 |  | 0
2017-09-18 | 215.5125 | [6 empty] | 165 |  | 0
2017-09-19 | 236.112 | [6 empty] | 410 |  | 0
2017-09-20 | 274.269 | [6 empty] | 0 |  | 0
2017-09-21 | 190.045 | [6 empty] | 0 |  | 0
2017-09-22 | 268.445 | [6 empty] | 0 |  | 0
2017-09-23 | 191.051 | [6 empty] | 0 |  | 0
2017-09-24 | 234.1855 | [6 empty] | 0 |  | 0
2017-09-25 | 234.1855 | [6 empty] | 425 |  | 0
2017-09-26 | 228.401 | [6 empty] | 0 |  | 0
2017-09-27 | 231.651 | [6 empty] | 0 |  | 0
2017-09-28 | 290.218 | [6 empty] | 0 |  | 0
2017-09-29 | 213.135 | [6 empty] | 0 |  | 0
2017-09-30 | 241.872 | [6 empty] | 0 |  | 0
2017-10-01 | 197.4855 | [6 empty] | 0 |  | 0
2017-10-02 | 319.1193 | [6 empty] | 0 |  | 2
2017-10-03 | 342.694 | [6 empty] | 0 |  | 27
2017-10-04 | 362.7948 | [6 empty] | 0 |  | 0
2017-10-05 | 257.788 | [6 empty] | 0 |  | 0
2017-10-06 | 284.064 | [6 empty] | 0 |  | 0
2017-10-07 | 185.847 | [6 empty] | 0 |  | 6
2017-10-08 | 241.926 | [6 empty] | 0 |  | 0
2017-10-09 | 241.926 | 5 | 225 | 1 | 14 | 5 | 4.6 | 0 | 1 | 7 | 8.30am | 2017-10-09 | 2017-10-24
2017-10-10 | 271.53 | [6 empty] | 0 |  | 0
2017-10-11 | 246.368 | [6 empty] | 0 |  | 0
2017-10-12 | 222.528 | [6 empty] | 0 |  | 0
2017-10-13 | 247.72 | [6 empty] | 0 |  | 8
2017-10-14 | 260.756 | [6 empty] | 0 |  | 0
2017-10-15 | 487.857 | [6 empty] | 0 |  | 0
2017-10-16 | 678.2433 | [6 empty] | 0 |  | 0
2017-10-17 | 725.0053 | [6 empty] | 0 |  | 20
2017-10-18 | 702.0703 | [6 empty] | 0 |  | 5
2017-10-19 | 419.052 | [6 empty] | 0 |  | 2
2017-10-20 | 311.796 | [6 empty] | 0 |  | 0
2017-10-21 | 357.917 | [6 empty] | 0 |  | 29
2017-10-22 | 740.8785 | [6 empty] | 0 |  | 0
2017-10-23 | 740.8785 | [6 empty] | 0 |  | 0
2017-10-24 | 410.46 | [6 empty] | 0 |  | 0
2017-10-25 | 364.052 | [6 empty] | 0 |  | 0
2017-10-26 | 279.071 | [6 empty] | 0 |  | 4
2017-10-27 | 227.788 | [6 empty] | 0 |  | 0
2017-10-28 | 320.097 | [6 empty] | 0 |  | 0
2017-10-29 | 308.09 | [6 empty] | 0 |  | 0
2017-10-30 | 308.09 | [6 empty] | 0 |  | 0
2017-10-31 | 232.29 | [6 empty] | 0 |  | 0
2017-11-01 | 207.489 | [6 empty] | 0 |  | 0
2017-11-02 | 287.822 | [6 empty] | 0 |  | 0
2017-11-03 | 292.104 | [6 empty] | 0 |  | 0
2017-11-04 | 207.639 | [6 empty] | 0 |  | 0
2017-11-05 | 335.975 | [6 empty] | 0 |  | 0
2017-11-06 | 335.975 | 10 | 1 | 1 | 35 | 5.4 | 2.2 | 0 | 201 | 30 | 10.00am | 2017-11-06 | 2017-11-15 | Algal Bloom in Tertiary Ponds
2017-11-07 | 494.787 | [6 empty] | 0 |  | 25
2017-11-08 | 428.25 | [6 empty] | 0 |  | 19
2017-11-09 | 347.25 | [6 empty] | 0 |  | 0
2017-11-10 | 348.124 | [6 empty] | 0 |  | 10
2017-11-11 | 505.593 | [6 empty] | 0 |  | 11
2017-11-12 | 469.0785 | [6 empty] | 0 |  | 0
2017-11-13 | 469.0785 | [6 empty] | 0 |  | 5
2017-11-14 | 332.695 | [6 empty] | 0 |  | 0
2017-11-15 | 317.553 | [6 empty] | 0 |  | 0
2017-11-16 | 308.425 | [6 empty] | 0 |  | 0
2017-11-17 | 343.757 | [6 empty] | 0 |  | 0
2017-11-18 | 261.305 | [6 empty] | 0 |  | 0
2017-11-19 | 280.72 | [6 empty] | 0 |  | 0
2017-11-20 | 280.72 | [6 empty] | 0 |  | 3
2017-11-21 | 306.498 | [6 empty] | 0 |  | 0
2017-11-22 | 295.029 | [6 empty] | 0 |  | 10
2017-11-23 | 294.81 | [6 empty] | 0 |  | 0
2017-11-24 | 281.378 | [6 empty] | 0 |  | 0
2017-11-25 | 283.615 | [6 empty] | 0 |  | 3
2017-11-26 | 282.845 | [6 empty] | 0 |  | 0
2017-11-27 | 282.845 | [6 empty] | 0 |  | 0
2017-11-28 | 265.992 | [6 empty] | 0 |  | 0
2017-11-29 | 268.345 | [6 empty] | 0 |  | 0
2017-11-30 | 349.446 | [6 empty] | 0 |  | 3
2017-12-01 | 314.793 | [6 empty] | 0 |  | 0
2017-12-02 | 244.455 | [6 empty] | 0 |  | 4
2017-12-03 | 296.542 | [6 empty] | 0 |  | 0
2017-12-04 | 296.542 | 13 | 1 | 1 | 45 | 4.1 | 1.6 | 0 | 1 | 8 | 13:30 | 2017-12-19 | 2017-12-19 | Algal Bloom in Tertiary Ponds
2017-12-05 | 310.218 | [6 empty] | 0 |  | 9
2017-12-06 | 487.261 | [6 empty] | 0 |  | 12
2017-12-07 | 350.428 | [6 empty] | 0 |  | 0
2017-12-08 | 278.959 | [6 empty] | 0 |  | 0
2017-12-09 | 306.308 | [6 empty] | 0 |  | 0
2017-12-10 | 279.578 | [6 empty] | 0 |  | 0
2017-12-11 | 279.578 | [6 empty] | 0 |  | 6
2017-12-12 | 268.532 | [6 empty] | 0 |  | 0
2017-12-13 | 264.448 | [6 empty] | 0 |  | 0
2017-12-14 | 268.285 | [6 empty] | 0 |  | 0
2017-12-15 | 310.946 | [6 empty] | 0 |  | 0
2017-12-16 | 217.089 | [6 empty] | 0 |  | 0
2017-12-17 | 260.0345 | [6 empty] | 0 |  | 0
2017-12-18 | 260.0345 | [6 empty] | 0 |  | 0
2017-12-19 | 256.082 | [6 empty] | 0 |  | 0
2017-12-20 | 248.929 | [6 empty] | 0 |  | 0
2017-12-21 | 263.291 | [6 empty] | 0 |  | 0
2017-12-22 | 415.178 | [6 empty] | 0 |  | 35
2017-12-23 | 347.803 | [6 empty] | 0 |  | 0
2017-12-24 | 273.412 | [6 empty] | 0 |  | 0
2017-12-25 | 785.62 | [6 empty] | 0 |  | 0
2017-12-26 | 785.62 | [6 empty] | 0 |  | 90
2017-12-27 | 718.287 | [6 empty] | 0 |  | 6
2017-12-28 | 479.264 | [6 empty] | 0 |  | 7
2017-12-29 | 394.169 | [6 empty] | 0 |  | 0
2017-12-30 | 389.799 | [6 empty] | 0 |  | 0
2017-12-31 | 463.1945 | [6 empty] | 0 |  | 0
2018-01-01 | 463.1945 | [6 empty] | 0 |  | 21
2018-01-02 | 359.369 | 22 | 649 | 1 | 71 | 7.2 | 1.7 | 0 | 1 | 4 | 8:30 | 2018-01-09 | 2018-01-09 | Algal Bloom in Tertiary Ponds
2018-01-03 | 1042.412 | [6 empty] | 0 |  | 35
2018-01-04 | 641.647 | [6 empty] | 0 |  | 0
2018-01-05 | 453.55 | [6 empty] | 0 |  | 0
2018-01-06 | 408.913 | [6 empty] | 0 |  | 0
2018-01-07 | 315.033 | [6 empty] | 0 |  | 0
2018-01-08 | 315.033 | [6 empty] | 0 |  | 0
2018-01-09 | 316.79 | [6 empty] | 0 |  | 0
2018-01-10 | 302.376 | [6 empty] | 0 |  | 0
2018-01-11 | 290.238 | [6 empty] | 0 |  | 0
2018-01-12 | 323.727 | [6 empty] | 0 |  | 0
2018-01-13 | 285.103 | [6 empty] | 0 |  | 0
2018-01-14 | 256.129 | [6 empty] | 0 |  | 0
2018-01-15 | 256.129 | [6 empty] | 0 |  | 0
2018-01-16 | 254.947 | [6 empty] | 0 |  | 0
2018-01-17 | 266.984 | [6 empty] | 0 |  | 0
2018-01-18 | 265.747 | [6 empty] | 0 |  | 0
2018-01-19 | 264.141 | [6 empty] | 0 |  | 0
2018-01-20 | 260.352 | [6 empty] | 0 |  | 0
2018-01-21 | 257.4745 | [6 empty] | 0 |  | 0
2018-01-22 | 257.4745 | [6 empty] | 0 |  | 0
2018-01-23 | 256.504 | [6 empty] | 0 |  | 0
2018-01-24 | 296.69 | [6 empty] | 0 |  | 0
2018-01-25 | 259.053 | [6 empty] | 0 |  | 0
2018-01-26 | 250.842 | [6 empty] | 0 |  | 0
2018-01-27 | 252.387 | [6 empty] | 0 |  | 0
2018-01-28 | 281.2595 | [6 empty] | 0 |  | 0
2018-01-29 | 281.2595 | [6 empty] | 0 |  | 4
2018-01-30 | 227.393 | [6 empty] | 0 |  | 6
2018-01-31 | 256.733 | [6 empty] | 0 |  | 0
2018-02-01 | 340.944 | [6 empty] | 0 |  | 21
2018-02-02 | 329.105 | [6 empty] | 0 |  | 11
2018-02-03 | 316.007 | [6 empty] | 0 |  | 9
2018-02-04 | 418.141 | [6 empty] | 0 |  | 0
2018-02-05 | 418.141 | [6 empty] | 0 |  | 21
2018-02-06 | 311.233 | [6 empty] | 0 |  | 0
2018-02-07 | 270.853 | [6 empty] | 0 |  | 4
2018-02-08 | 272.822 | [6 empty] | 0 |  | 3
2018-02-09 | 313.996 | [6 empty] | 0 |  | 2
2018-02-10 | 202.334 | [6 empty] | 0 |  | 0
2018-02-11 | 261.805 | [6 empty] | 0 |  | 0
2018-02-12 | 261.805 | [6 empty] | 0 |  | 0
2018-02-13 | 0 | [6 empty] | 0 |  | 0
2018-02-14 | 506.322 | [6 empty] | 0 |  | 0
2018-02-15 | 237.329 | [6 empty] | 0 |  | 0
2018-02-16 | 249.366 | [6 empty] | 0 |  | 0
2018-02-17 | 301.859 | [6 empty] | 0 |  | 0
2018-02-18 | 226.5655 | [6 empty] | 0 |  | 0
2018-02-19 | 226.5655 | [6 empty] | 0 |  | 0
2018-02-20 | 255.115 | [6 empty] | 0 |  | 0
2018-02-21 | 340.161 | [6 empty] | 0 |  | 21
2018-02-22 | 193.268 | [6 empty] | 0 |  | 0
2018-02-23 | 368.275 | [6 empty] | 0 |  | 16
2018-02-24 | 456.376 | [6 empty] | 0 |  | 30
2018-02-25 | 510.7845 | [6 empty] | 0 |  | 0
2018-02-26 | 510.7845 | 27 | 1 | 1 | 124 | 10 | 1.7 | 0 | 1 | 6 | 9:30 | 2018-03-07 | 2018-03-07 | High Inflow through plant
2018-02-27 | 844.791 | [6 empty] | 0 |  | 40
2018-02-28 | 453.175 | [6 empty] | 0 |  | 0
2018-03-01 | 0.5 | [6 empty] | 0 |  | 0
2018-03-02 | 306.381 | [6 empty] | 0 |  | 0
2018-03-03 | 332.605 | [6 empty] | 0 |  | 0
2018-03-04 | 279.097 | [6 empty] | 0 |  | 0
2018-03-05 | 279.097 | [6 empty] | 0 |  | 0
2018-03-06 | 397.059 | [6 empty] | 0 |  | 30
2018-03-07 | 1438.862 | [6 empty] | 0 |  | 64
2018-03-08 | 1611.034 | [6 empty] | 0 |  | 7
2018-03-09 | 686.499 | [6 empty] | 0 |  | 9
2018-03-10 | 596.414 | [6 empty] | 0 |  | 3
2018-03-11 | 530.258 | [6 empty] | 0 |  | 0
2018-03-12 | 530.258 | [6 empty] | 0 |  | 0
2018-03-13 | 412.292 | [6 empty] | 0 |  | 0
2018-03-14 | 421.184 | [6 empty] | 0 |  | 13
2018-03-15 | 407.783 | [6 empty] | 0 |  | 0
2018-03-16 | 370.866 | [6 empty] | 0 |  | 0
2018-03-17 | 414.323 | [6 empty] | 0 |  | 0
2018-03-18 | 325.69 | [6 empty] | 0 |  | 0
2018-03-19 | 325.69 | [6 empty] | 0 |  | 0
2018-03-20 | 373.591 | [6 empty] | 0 |  | 0
2018-03-21 | 262.301 | [6 empty] | 0 |  | 2
2018-03-22 | 303.455 | [6 empty] | 0 |  | 6
2018-03-23 | 453.089 | [6 empty] | 0 |  | 16
2018-03-24 | 411.719 | [6 empty] | 0 |  | 9
2018-03-25 | 667.5755 | [6 empty] | 0 |  | 0
2018-03-26 | 667.5755 | 25 | 35 | 1 | 22 | 7 | 1.7 | 0 | 1 | 8 | 11:30 | 2018-04-13 | 2018-04-13 | High Inflow through plant
2018-03-27 | 451.837 | [6 empty] | 0 |  | 0
2018-03-28 | 412.826 | [6 empty] | 0 |  | 1
2018-03-29 | 318.382 | [6 empty] | 0 |  | 5
2018-03-30 | 291.105 | [6 empty] | 0 |  | 3
2018-03-31 | 399.888 | [6 empty] | 0 |  | 0
2018-04-01 | 339.288 | [6 empty] | 0 |  | 0
2018-04-02 | 339.288 | [6 empty] | 0 |  | 0
2018-04-03 | 334.109 | [6 empty] | 0 |  | 4
2018-04-04 | 361.179 | [6 empty] | 0 |  | 3
2018-04-05 | 370.352 | [6 empty] | 0 |  | 2
2018-04-06 | 251.113 | [6 empty] | 0 |  | 4
2018-04-07 | 262.539 | [6 empty] | 0 |  | 0
2018-04-08 | 310.5375 | [6 empty] | 0 |  | 0
2018-04-09 | 310.5375 | [6 empty] | 0 |  | 0
2018-04-10 | 290.113 | [6 empty] | 0 |  | 0
2018-04-11 | 268.341 | [6 empty] | 0 |  | 0
2018-04-12 | 292.315 | [6 empty] | 0 |  | 0
2018-04-13 | 281.916 | [6 empty] | 0 |  | 0
2018-04-14 | 295.726 | [6 empty] | 0 |  | 0
2018-04-15 | 268.341 | [6 empty] | 0 |  | 0
2018-04-16 | 244.321 | [6 empty] | 0 |  | 0
2018-04-17 | 259.638 | [6 empty] | 0 |  | 0
2018-04-18 | 323.171 | [6 empty] | 0 |  | 18
2018-04-19 | 293.844 | 23 | 1 | 1 | 34 | 6.7 | 2.5 | 0 |  | 0 | 11:30 | 2018-05-04 | 2018-05-04 | Algal Bloom in Tertiary Ponds
2018-04-20 | 330.661 | [6 empty] | 0 |  | 0
2018-04-21 | 210.084 | [6 empty] | 0 |  | 0
2018-04-22 | 324.5235 | [6 empty] | 0 |  | 0
2018-04-23 | 324.5235 | [6 empty] | 0 | 1 | 0 | 9.00am | 2018-05-04 | 2018-05-04
2018-04-24 | 300.697 | [6 empty] | 0 |  | 0
2018-04-25 | 490.175 | [6 empty] | 0 |  | 21
2018-04-26 | 403.542 | [6 empty] | 0 |  | 5
2018-04-27 | 348.836 | [6 empty] | 0 |  | 0
2018-04-28 | 330.353 | [6 empty] | 0 |  | 15
2018-04-29 | 300.371 | [6 empty] | 0 |  | 0
2018-04-30 | 300.371 | [6 empty] | 0 |  | 5
2018-05-01 | 324.186 | [6 empty] | 0 |  | 2
2018-05-02 | 303.899 | [6 empty] | 0 |  | 0
2018-05-03 | 278.751 | [6 empty] | 0 |  | 0
2018-05-04 | 335.091 | [6 empty] | 0 |  | 0
2018-05-05 | 217.087 | [6 empty] | 0 |  | 0
2018-05-06 | 295.831 | [6 empty] | 0 |  | 0
2018-05-07 | 295.831 | [6 empty] | 0 |  | 0
2018-05-08 | 308.663 | [6 empty] | 0 |  | 8
2018-05-09 | 362.96 | [6 empty] | 0 |  | 5
2018-05-10 | 312.362 | [6 empty] | 0 |  | 0
2018-05-11 | 298.407 | [6 empty] | 0 |  | 0
2018-05-12 | 254.247 | [6 empty] | 0 |  | 0
2018-05-13 | 281.6055 | [6 empty] | 0 |  | 0
2018-05-14 | 281.6055 | [6 empty] | 0 |  | 0
2018-05-15 | 278.009 | [6 empty] | 0 |  | 0
2018-05-16 | 258.883 | [6 empty] | 0 |  | 0
2018-05-17 | 278.089 | [6 empty] | 0 |  | 0
2018-05-18 | 293.756 | [6 empty] | 0 |  | 2
2018-05-19 | 204.375 | [6 empty] | 0 |  | 0
2018-05-20 | 261.1875 | [6 empty] | 0 |  | 0
2018-05-21 | 261.1875 | [6 empty] | 0 |  | 0
2018-05-22 | 250.45 | 19 | 10 | 1 | 8 | 4.6 | 2.5 | 0 | 10 | 0 | 10:30 | 2018-06-06 | 2018-06-06
2018-05-23 | 242.424 | [6 empty] | 0 |  | 0
2018-05-24 | 259.63 | [6 empty] | 0 |  | 0
2018-05-25 | 237.418 | [6 empty] | 0 |  | 0
2018-05-26 | 269.26 | [6 empty] | 0 |  | 0
2018-05-27 | 271.4 | [6 empty] | 0 |  | 0
2018-05-28 | 289.72 | [6 empty] | 0 |  | 0
2018-05-29 | 267.32 | [6 empty] | 0 |  | 0
2018-05-30 | 267.97 | [6 empty] | 0 |  | 0
2018-05-31 | 254.91 | [6 empty] | 0 |  | 0
2018-06-01 | 240.9 | [6 empty] | 0 |  | 0
2018-06-02 | 237 | [6 empty] | 0 |  | 0
2018-06-03 | 251 | [6 empty] | 0 |  | 0
2018-06-04 | 251 | [6 empty] | 0 |  | 0
2018-06-05 | 244 | [6 empty] | 0 |  | 0
2018-06-06 | 249 | [6 empty] | 0 |  | 0
2018-06-07 | 304 | [6 empty] | 0 |  | 26
2018-06-08 | 327 | [6 empty] | 0 |  | 0
2018-06-09 | 183.013 | [6 empty] | 0 |  | 4
2018-06-10 | 348.0645 | [6 empty] | 0 |  | 0
2018-06-11 | 348.0645 | [6 empty] | 0 |  | 0
2018-06-12 | 357.64 | [6 empty] | 0 |  | 6
2018-06-13 | 289.401 | [6 empty] | 0 |  | 0
2018-06-14 | 270.67 | [6 empty] | 0 |  | 0
2018-06-15 | 255.145 | [6 empty] | 0 |  | 0
2018-06-16 | 200.806 | [6 empty] | 0 |  | 0
2018-06-17 | 275.3325 | [6 empty] | 0 |  | 0
2018-06-18 | 275.3325 | [6 empty] | 0 |  | 0
2018-06-19 | 237.048 | [6 empty] | 0 |  | 0
2018-06-20 | 235.631 | [6 empty] | 0 |  | 0
2018-06-21 | 270.393 | [6 empty] | 0 |  | 0
2018-06-22 | 228.333 | [6 empty] | 0 |  | 0
2018-06-23 | 240.227 | [6 empty] | 0 |  | 0
2018-06-24 | 244.2505 | [6 empty] | 0 |  | 0
2018-06-25 | 244.2505 | [6 empty] | 0 |  | 0
2018-06-26 | 235.687 | 3 | 23 | 2 | 12 | 5.9 | 3.9 | 0 | <1 | 0 | 11:30 | 2018-07-05 | 2018-07-05
2018-06-27 | 226.362 | [6 empty] | 0 |  | 0
2018-06-28 | 245.744 | [6 empty] | 0 |  | 0
2018-06-29 | 276.33 | [6 empty] | 0 |  | 0
2018-06-30 | 183.028 | [6 empty] | 0 |  | 0
2018-07-01 | 253.896 | [6 empty] | 0 |  | 0
2018-07-02 | 253.896 | [6 empty] | 0 |  | 0
2018-07-03 | 224.946 | [6 empty] | 0 |  | 0
2018-07-04 | 289.078 | [6 empty] | 0 |  | 8
2018-07-05 | 307.475 | [6 empty] | 0 |  | 10
2018-07-06 | 293.819 | [6 empty] | 0 |  | 3
2018-07-07 | 274.892 | [6 empty] | 0 |  | 0
2018-07-08 | 270.5715 | [6 empty] | 0 |  | 0
2018-07-09 | 270.5715 | [6 empty] | 0 |  | 0
2018-07-10 | 245.134 | [6 empty] | 0 |  | 0
2018-07-11 | 239.93 | [6 empty] | 0 |  | 3
2018-07-12 | 237.488 | [6 empty] | 0 |  | 2
2018-07-13 | 292.16 | [6 empty] | 0 |  | 1
2018-07-14 | 177.082 | [6 empty] | 0 |  | 0
2018-07-15 | 246.5905 | [6 empty] | 0 |  | 0
2018-07-16 | 246.5905 | [6 empty] | 0 |  | 0
2018-07-17 | 238.424 | [6 empty] | 0 |  | 0
2018-07-18 | 237.869 | [6 empty] | 0 |  | 0
2018-07-19 | 225.961 | [6 empty] | 0 |  | 0
2018-07-20 | 236.413 | [6 empty] | 0 |  | 0
2018-07-21 | 220.205 | [6 empty] | 0 |  | 0
2018-07-22 | 238.007 | [6 empty] | 0 |  | 0
2018-07-23 | 238.007 | [6 empty] | 0 |  | 0
2018-07-24 | 244.154 | 2 | 180 | 2 | 2 | 10 | 5.3 | 0 | 0 | 0 | 10:00 | 2018-08-07 | 2018-08-07
2018-07-25 | 228.001 | [6 empty] | 0 |  | 0
2018-07-26 | 224.52 | [6 empty] | 0 |  | 0
2018-07-27 | 274.772 | [6 empty] | 0 |  | 0
2018-07-28 | 185.117 | [6 empty] | 0 |  | 0
2018-07-29 | 259.7555 | [6 empty] | 0 |  | 0
2018-07-30 | 259.7555 | [6 empty] | 0 |  | 0
2018-07-31 | 233.04 | [6 empty] | 0 |  | 0
2018-08-01 | 219.21 | [6 empty] | 0 |  | 0
2018-08-02 | 229.937 | [6 empty] | 0 |  | 0
2018-08-03 | 214.365 | [6 empty] | 0 |  | 0
2018-08-04 | 214.257 | [6 empty] | 0 |  | 0
2018-08-05 | 236.712 | [6 empty] | 0 |  | 0
2018-08-06 | 236.712 | [6 empty] | 0 |  | 0
2018-08-07 | 224.757 | [6 empty] | 0 |  | 0
2018-08-08 | 228.083 | [6 empty] | 0 |  | 0
2018-08-09 | 229.862 | [6 empty] | 0 |  | 0
2018-08-10 | 253.756 | [6 empty] | 0 |  | 0
2018-08-11 | 152.859 | [6 empty] | 0 |  | 0
2018-08-12 | 237.5745 | [6 empty] | 0 |  | 0
2018-08-13 | 237.5745 | [6 empty] | 0 |  | 0
2018-08-14 | 201.83 | [6 empty] | 0 |  | 0
2018-08-15 | 232.23 | [6 empty] | 0 |  | 0
2018-08-16 | 190.901 | [6 empty] | 0 |  | 0
2018-08-17 | 194.702 | [6 empty] | 0 |  | 0
2018-08-18 | 208.4772 | [6 empty] | 0 |  | 0
2018-08-19 | 208.4772 | [6 empty] | 0 |  | 0
2018-08-20 | 215.6905 | [6 empty] | 0 |  | 0
2018-08-21 | 220.834 | 5 | 40 | 1 | 5 | 8.6 | 4.2 | 0 | 0 | 0 | 11:00 | 2018-09-11 | 2018-09-11
2018-08-22 | 207.512 | [6 empty] | 0 |  | 0
2018-08-23 | 209.584 | [6 empty] | 0 |  | 0
2018-08-24 | 244.41 | [6 empty] | 0 |  | 0
2018-08-25 | 208.1625 | [6 empty] | 0 |  | 0
2018-08-26 | 208.1625 | [6 empty] | 0 |  | 0
2018-08-27 | 250.862 | [6 empty] | 0 |  | 15
2018-08-28 | 247.2 | [6 empty] | 0 |  | 5
2018-08-29 | 233.166 | [6 empty] | 0 |  | 0
2018-08-30 | 222.172 | [6 empty] | 0 |  | 0
2018-08-31 | 208.701 | [6 empty] | 0 |  | 0
MINIMUM | 0 | 2 | 1 | 1 | 2 | 4.1 | 1.6 | 0 | 0 | 0
AVERAGE | 312.0764 | 13 | 98.8333 | 1.1667 | 31.8333 | 6.7 | 2.9417 | 3.8926 | 19.8182 | 2.7753
MAXIMUM | 1611.034 | 27 | 649 | 2 | 124 | 10 | 5.3 | 425 | 201 | 90
TOTAL | 113907.8787 | [6 empty] | 1413 |  | 1013
SAMPLE COUNT |  | 12
Non-compliant Results | 2 | 4 |  | 0 | 5 |  |  |  | 0

## 18-19
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 18/19
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2018-09-01 | 227.147 | [6 empty] | 0 | 0 | 0
2018-09-02 | 234.073 | [6 empty] | 0 | 0 | 0
2018-09-03 | 234.073 | [6 empty] | 0 | 0 | 10
2018-09-04 | 264.572 | [6 empty] | 0 | 0 | 17
2018-09-05 | 334.819 | [6 empty] | 0 | 0 | 14
2018-09-06 | 299.617 | [6 empty] | 0 | 0 | 8
2018-09-07 | 291.412 | [6 empty] | 0 | 0 | 0
2018-09-08 | 177.828 | [6 empty] | 0 | 0 | 0
2018-09-09 | 242.1735 | [6 empty] | 0 | 0 | 0
2018-09-10 | 242.1735 | [6 empty] | 0 | 0 | 0
2018-09-11 | 243.174 | [6 empty] | 0 | 0 | 0
2018-09-12 | 214.229 | [6 empty] | 0 | 0 | 0
2018-09-13 | 218.113 | [6 empty] | 0 | 0 | 0
2018-09-14 | 208.874 | [6 empty] | 0 | 0 | 0
2018-09-15 | 217.129 | [6 empty] | 0 | 0 | 0
2018-09-16 | 221.043 | [6 empty] | 0 | 0 | 0
2018-09-17 | 221.043 | [6 empty] | 0 | 0 | 0
2018-09-18 | 214.559 | [6 empty] | 0 | 0 | 0
2018-09-19 | 213.636 | [6 empty] | 0 | 0 | 0
2018-09-20 | 225 | [6 empty] | 0 | 0 | 0
2018-09-21 | 263 | [6 empty] | 0 | 0 | 2
2018-09-22 | 166 | [6 empty] | 0 | 0 | 0
2018-09-23 | 234.5 | [6 empty] | 0 | 0 | 0
2018-09-24 | 234.5 | [6 empty] | 0 | 0 | 0
2018-09-25 | 218 | 12 | 60 | 2 | 16 | 5.8 | 4 | 111 | 90 | 0 | 9:00 | 2018-10-08 | 2018-10-08
2018-09-26 | 224 | [6 empty] | 0 | 0 | 0
2018-09-27 | 250 | [6 empty] | 0 | 0 | 0
2018-09-28 | 204 | [6 empty] | 0 | 0 | 0
2018-09-29 | 226 | [6 empty] | 0 | 0 | 0
2018-09-30 | 217 | [6 empty] | 0 | 0 | 0
2018-10-01 | 217 | [6 empty] | 0 | 0 | 0
2018-10-02 | 247 | [6 empty] | 0 | 0 | 0
2018-10-03 | 226 | [6 empty] | 0 | 0 | 0
2018-10-04 | 251 | [6 empty] | 0 | 0 | 0
2018-10-05 | 200 | [6 empty] | 0 | 0 | 0
2018-10-06 | 167 | [6 empty] | 0 | 0 | 0
2018-10-07 | 224 | [6 empty] | 0 | 0 | 0
2018-10-08 | 224 | [6 empty] | 0 | 0 | 0
2018-10-09 | 218 | [6 empty] | 0 | 0 | 0
2018-10-10 | 207 | [6 empty] | 0 | 0 | 0
2018-10-11 | 282 | [6 empty] | 0 | 0 | 22
2018-10-12 | 429 | [6 empty] | 0 | 0 | 30
2018-10-13 | 409 | [6 empty] | 0 | 0 | 0
2018-10-14 | 976.5 | [6 empty] | 0 | 0 | 0
2018-10-15 | 976.5 | [6 empty] | 0 | 0 | 68
2018-10-16 | 1397 | [6 empty] | 0 | 0 | 15
2018-10-17 | 1102 | [6 empty] | 0 | 0 | 37
2018-10-18 | 1481 | [6 empty] | 0 | 0 | 8
2018-10-19 | 725 | [6 empty] | 0 | 0 | 2
2018-10-20 | 540 | [6 empty] | 0 | 0 | 0
2018-10-21 | 467 | [6 empty] | 0 | 0 | 0
2018-10-22 | 436 | [6 empty] | 0 | 0 | 8
2018-10-23 | 430 | 6 | <10 | 2 | 11 | 7.2 | 5.2 | 82 | 70 | 0 | 10:00 | 2018-11-06 | 2018-11-06
2018-10-24 | 371 | [6 empty] | 0 | 0 | 0
2018-10-25 | 350 | [6 empty] | 0 | 0 | 0
2018-10-26 | 344 | [6 empty] | 0 | 0 | 4
2018-10-27 | 363 | [6 empty] | 0 | 0 | 0
2018-10-28 | 333 | [6 empty] | 0 | 0 | 0
2018-10-29 | 322 | [6 empty] | 0 | 0 | 3
2018-10-30 | 318 | [6 empty] | 0 | 0 | 0
2018-10-31 | 300 | [6 empty] | 0 | 0 | 0
2018-11-01 | 290 | [6 empty] | 0 | 0 | 0
2018-11-02 | 306 | [6 empty] | 0 | 0 | 0
2018-11-03 | 288 | [6 empty] | 0 | 0 | 0
2018-11-04 | 287 | [6 empty] | 0 | 0 | 0
2018-11-05 | 271 | [6 empty] | 0 | 0 | 0
2018-11-06 | 284 | [6 empty] | 0 | 0 | 0
2018-11-07 | 298 | [6 empty] | 0 | 0 | 0
2018-11-08 | 267 | [6 empty] | 0 | 0 | 0
2018-11-09 | 286 | [6 empty] | 0 | 0 | 0
2018-11-10 | 289 | [6 empty] | 0 | 0 | 0
2018-11-11 | 307 | [6 empty] | 0 | 0 | 0
2018-11-12 | 283 | [6 empty] | 0 | 0 | 8
2018-11-13 | 258 | [6 empty] | 0 | 0 | 0
2018-11-14 | 285 | [6 empty] | 0 | 0 | 0
2018-11-15 | 330 | [6 empty] | 0 | 0 | 0
2018-11-16 | 344 | [6 empty] | 0 | 0 | 9
2018-11-17 | 443 | [6 empty] | 0 | 0 | 0
2018-11-18 | 419 | [6 empty] | 0 | 0 | 0
2018-11-19 | 381 | [6 empty] | 0 | 0 | 23
2018-11-20 | 356 | 17 | <10 | 2 | 61 | 9.1 | 1.9 | 394 | 10 | 0 | 10:00 | 2018-11-28 | 2018-11-28
2018-11-21 | 353 | [6 empty] | 0 | 0 | 0
2018-11-22 | 407 | [6 empty] | 0 | 0 | 9
2018-11-23 | 330 | [6 empty] | 0 | 0 | 9
2018-11-24 | 292 | [6 empty] | 0 | 0 | 0
2018-11-25 | 310 | [6 empty] | 0 | 0 | 0
2018-11-26 | 295 | [6 empty] | 0 | 0 | 0
2018-11-27 | 347 | [6 empty] | 0 | 0 | 0
2018-11-28 | 388 | [6 empty] | 0 | 0 | 0
2018-11-29 | 363 | [6 empty] | 0 | 0 | 0
2018-11-30 | 350 | [6 empty] | 0 | 0 | 0
2018-12-01 | 356 | [6 empty] | 0 | 0 | 0
2018-12-02 | 359 | [6 empty] | 0 | 0 | 0
2018-12-03 | 326 | [6 empty] | 0 | 0 | 0
2018-12-04 | 332 | [6 empty] | 0 | 0 | 0
2018-12-05 | 318 | [6 empty] | 0 | 0 | 0
2018-12-06 | 295 | [6 empty] | 0 | 0 | 0
2018-12-07 | 295 | [6 empty] | 0 | 0 | 0
2018-12-08 | 286 | [6 empty] | 0 | 0 | 0
2018-12-09 | 364 | [6 empty] | 0 | 0 | 0
2018-12-10 | 336 | [6 empty] | 0 | 0 | 0
2018-12-11 | 318 | [6 empty] | 0 | 0 | 0
2018-12-12 | 315 | [6 empty] | 0 | 0 | 0
2018-12-13 | 320 | [6 empty] | 0 | 0 | 3
2018-12-14 | 316 | [6 empty] | 0 | 0 | 0
2018-12-15 | 318 | [6 empty] | 0 | 0 | 4
2018-12-16 | 292 | [6 empty] | 0 | 0 | 0
2018-12-17 | 277 | [6 empty] | 0 | 0 | 5
2018-12-18 | 263 | [6 empty] | 0 | 0 | 15
2018-12-19 | 270 | [6 empty] | 0 | 0 | 7
2018-12-20 | 297 | [6 empty] | 0 | 0 | 6
2018-12-21 | 301 | [6 empty] | 0 | 0 | 15
2018-12-22 | 428 | [6 empty] | 0 | 0 | 0
2018-12-23 | 297 | [6 empty] | 0 | 0 | 0
2018-12-24 | 280 | 17 | <10 | 2 | 23 | 5 | 1.8 | 40 | 10 | 0 | 10:30 | 2019-01-10 | 2019-01-10
2018-12-25 | 258 | [6 empty] | 0 | 0 | 0
2018-12-26 | 278 | [6 empty] | 0 | 0 | 0
2018-12-27 | 273 | [6 empty] | 0 | 0 | 0
2018-12-28 | 263 | [6 empty] | 0 | 0 | 0
2018-12-29 | 251 | [6 empty] | 0 | 0 | 0
2018-12-30 | 262 | [6 empty] | 0 | 0 | 0
2018-12-31 | 269 | [6 empty] | 0 | 0 | 0
2019-01-01 | 263 | [6 empty] | 0 | 0 | 0
2019-01-02 | 264 | [6 empty] | 0 | 0 | 0
2019-01-03 | 263 | [6 empty] | 0 | 0 | 0
2019-01-04 | 255 | [6 empty] | 0 | 0 | 0
2019-01-05 | 253 | [6 empty] | 0 | 0 | 0
2019-01-06 | 258 | [6 empty] | 0 | 0 | 0
2019-01-07 | 247 | [6 empty] | 0 | 0 | 0
2019-01-08 | 241 | [6 empty] | 0 | 0 | 0
2019-01-09 | 241 | [6 empty] | 0 | 0 | 0
2019-01-10 | 228 | [6 empty] | 0 | 0 | 0
2019-01-11 | 226 | [6 empty] | 0 | 0 | 0
2019-01-12 | 231 | [6 empty] | 0 | 0 | 0
2019-01-13 | 222 | [6 empty] | 0 | 0 | 0
2019-01-14 | 225 | [6 empty] | 0 | 0 | 0
2019-01-15 | 212 | [6 empty] | 0 | 0 | 0
2019-01-16 | 208 | [6 empty] | 0 | 0 | 0
2019-01-17 | 210 | [6 empty] | 0 | 0 | 0
2019-01-18 | 248 | [6 empty] | 0 | 0 | 0
2019-01-19 | 230 | [6 empty] | 0 | 0 | 0
2019-01-20 | 226 | [6 empty] | 0 | 0 | 0
2019-01-21 | 217 | 100% Re-use - Zero Discharge | [5 empty] | 0 | 0 | 0
2019-01-22 | 241 | [6 empty] | 0 | 0 | 0
2019-01-23 | 212 | [6 empty] | 0 | 0 | 10
2019-01-24 | 251 | [6 empty] | 0 | 0 | 0
2019-01-25 | 203 | [6 empty] | 0 | 0 | 0
2019-01-26 | 226 | [6 empty] | 0 | 0 | 0
2019-01-27 | 206 | [6 empty] | 0 | 0 | 0
2019-01-28 | 219 | [6 empty] | 0 | 0 | 0
2019-01-29 | 212 | [6 empty] | 0 | 0 | 0
2019-01-30 | 201 | [6 empty] | 0 | 0 | 0
2019-01-31 | 202 | [6 empty] | 0 | 0 | 0
2019-02-01 | 215 | [6 empty] | 0 | 0 | 0
2019-02-02 | 233 | [6 empty] | 0 | 0 | 0
2019-02-03 | 230 | [6 empty] | 0 | 0 | 0
2019-02-04 | 218 | [6 empty] | 0 | 0 | 0
2019-02-05 | 204 | [6 empty] | 0 | 0 | 0
2019-02-06 | 217 | [6 empty] | 0 | 0 | 8
2019-02-07 | 215 | [6 empty] | 0 | 0 | 4
2019-02-08 | 215 | [6 empty] | 0 | 0 | 0
2019-02-09 | 251 | [6 empty] | 0 | 0 | 0
2019-02-10 | 273 | [6 empty] | 0 | 0 | 0
2019-02-11 | 249 | [6 empty] | 0 | 0 | 0
2019-02-12 | 233 | [6 empty] | 0 | 0 | 0
2019-02-13 | 239 | [6 empty] | 0 | 0 | 0
2019-02-14 | 226 | [6 empty] | 0 | 0 | 0
2019-02-15 | 251 | [6 empty] | 0 | 0 | 0
2019-02-16 | 228 | [6 empty] | 0 | 0 | 0
2019-02-17 | 234 | [6 empty] | 0 | 0 | 0
2019-02-18 | 233 | [6 empty] | 0 | 0 | 0
2019-02-19 | 220 | 100% Re-use - Zero Discharge | [5 empty] | 0 | 0 | 0
2019-02-20 | 235 | [6 empty] | 0 | 0 | 0
2019-02-21 | 251 | [6 empty] | 0 | 0 | 0
2019-02-22 | 220 | [6 empty] | 0 | 0 | 25
2019-02-23 | 234 | [6 empty] | 0 | 0 | 3
2019-02-24 | 247 | [6 empty] | 0 | 0 | 0
2019-02-25 | 249 | [6 empty] | 0 | 0 | 6
2019-02-26 | 226 | [6 empty] | 0 | 0 | 5
2019-02-27 | 222 | [6 empty] | 0 | 0 | 0
2019-02-28 | 209 | [6 empty] | 0 | 0 | 0
2019-03-01 | 207 | [6 empty] | 0 | 0 | 0
2019-03-02 | 220 | [6 empty] | 0 | 0 | 2
2019-03-03 | 260 | [6 empty] | 0 | 0 | 0
2019-03-04 | 221 | [6 empty] | 0 | 0 | 0
2019-03-05 | 218 | [6 empty] | 0 | 0 | 0
2019-03-06 | 212 | [6 empty] | 0 | 0 | 0
2019-03-07 | 290 | [6 empty] | 0 | 0 | 0
2019-03-08 | 303 | [6 empty] | 0 | 0 | 26
2019-03-09 | 265 | [6 empty] | 0 | 0 | 0
2019-03-10 | 231 | [6 empty] | 0 | 0 | 0
2019-03-11 | 227 | [6 empty] | 0 | 0 | 0
2019-03-12 | 222 | [6 empty] | 0 | 0 | 0
2019-03-13 | 207 | [6 empty] | 0 | 0 | 0
2019-03-14 | 205 | [6 empty] | 0 | 0 | 0
2019-03-15 | 338 | [6 empty] | 0 | 0 | 3
2019-03-16 | 382 | [6 empty] | 0 | 0 | 45
2019-03-17 | 361 | [6 empty] | 0 | 0 | 0
2019-03-18 | 328 | [6 empty] | 0 | 0 | 24
2019-03-19 | 238 | 14 | 31 | 2 | 36 | 5.3 | 2.1 | 0 | 0 | 0 | 9:00 | 2019-03-28 | 2019-03-28
2019-03-20 | 230 | [6 empty] | 0 | 0 | 0
2019-03-21 | 214 | [6 empty] | 0 | 0 | 0
2019-03-22 | 202 | [6 empty] | 0 | 0 | 0
2019-03-23 | 234 | [6 empty] | 0 | 0 | 0
2019-03-24 | 238 | [6 empty] | 0 | 0 | 0
2019-03-25 | 200 | [6 empty] | 0 | 0 | 0
2019-03-26 | 198 | [6 empty] | 0 | 0 | 0
2019-03-27 | 306 | [6 empty] | 0 | 0 | 8
2019-03-28 | 254 | [6 empty] | 0 | 0 | 8
2019-03-29 | 207 | [6 empty] | 0 | 0 | 2
2019-03-30 | 214 | [6 empty] | 0 | 0 | 3
2019-03-31 | 222 | [6 empty] | 0 | 0 | 0
2019-04-01 | 206 | [6 empty] | 0 | 0 | 0
2019-04-02 | 826 | [6 empty] | 0 | 0 | 0
2019-04-03 | 452 | [6 empty] | 0 | 0 | 70
2019-04-04 | 295 | [6 empty] | 0 | 0 | 0
2019-04-05 | 256 | [6 empty] | 0 | 0 | 0
2019-04-06 | 267 | [6 empty] | 0 | 0 | 0
2019-04-07 | 249 | [6 empty] | 0 | 0 | 0
2019-04-08 | 232 | [6 empty] | 0 | 0 | 0
2019-04-09 | 224 | [6 empty] | 0 | 0 | 0
2019-04-10 | 228 | [6 empty] | 0 | 0 | 0
2019-04-11 | 249 | [6 empty] | 0 | 0 | 3
2019-04-12 | 281 | [6 empty] | 0 | 0 | 2
2019-04-13 | 238 | [6 empty] | 0 | 0 | 5
2019-04-14 | 230 | [6 empty] | 0 | 0 | 0
2019-04-15 | 265 | [6 empty] | 0 | 0 | 2
2019-04-16 | 325 | [6 empty] | 0 | 0 | 8
2019-04-17 | 308 | 16 | <1 | 2 | 20 | 7.3 | 1.6 | 0 | 0 | 5 | 10:00 | 2019-04-30 | 2019-04-30
2019-04-18 | 301 | [6 empty] | 0 | 0 | 3
2019-04-19 | 301 | [6 empty] | 0 | 0 | 0
2019-04-20 | 434 | [6 empty] | 0 | 0 | 0
2019-04-21 | 470 | [6 empty] | 0 | 0 | 0
2019-04-22 | 398 | [6 empty] | 0 | 0 | 0
2019-04-23 | 305 | [6 empty] | 0 | 0 | 0
2019-04-24 | 334 | [6 empty] | 0 | 0 | 0
2019-04-25 | 369 | [6 empty] | 0 | 0 | 0
2019-04-26 | 330 | [6 empty] | 0 | 0 | 0
2019-04-27 | 259 | [6 empty] | 0 | 0 | 0
2019-04-28 | 319 | [6 empty] | 0 | 0 | 0
2019-04-29 | 279 | [6 empty] | 0 | 0 | 0
2019-04-30 | 285 | [6 empty] | 0 | 0 | 0
2019-05-01 | 285 | [6 empty] | 0 | 0 | 3
2019-05-02 | 291 | [6 empty] | 0 | 0 | 8
2019-05-03 | 255 | [6 empty] | 0 | 0 | 0
2019-05-04 | 237 | [6 empty] | 0 | 0 | 0
2019-05-05 | 256 | [6 empty] | 0 | 0 | 0
2019-05-06 | 226 | [6 empty] | 0 | 0 | 3
2019-05-07 | 213 | [6 empty] | 0 | 0 | 0
2019-05-08 | 214 | [6 empty] | 0 | 0 | 0
2019-05-09 | 225 | [6 empty] | 0 | 0 | 0
2019-05-10 | 216 | [6 empty] | 0 | 0 | 0
2019-05-11 | 230 | [6 empty] | 0 | 0 | 0
2019-05-12 | 216 | [6 empty] | 0 | 0 | 0
2019-05-13 | 228 | [6 empty] | 0 | 0 | 5
2019-05-14 | 228 | 10 | <10 | 3 | 26 | 5.2 | 1.6 | 0 | 0 | 8 | 10:30 | 2019-05-21 | 2019-05-21
2019-05-15 | 212 | [6 empty] | 0 | 0 | 1
2019-05-16 | 209 | [6 empty] | 0 | 0 | 0
2019-05-17 | 213 | [6 empty] | 0 | 0 | 0
2019-05-18 | 257 | [6 empty] | 0 | 0 | 0
2019-05-19 | 237 | [6 empty] | 0 | 0 | 0
2019-05-20 | 262 | [6 empty] | 0 | 0 | 0
2019-05-21 | 265 | [6 empty] | 0 | 0 | 0
2019-05-22 | 295 | [6 empty] | 0 | 0 | 0
2019-05-23 | 264 | [6 empty] | 0 | 0 | 0
2019-05-24 | 275 | [6 empty] | 0 | 0 | 8
2019-05-25 | 260 | [6 empty] | 0 | 0 | 0
2019-05-26 | 324 | [6 empty] | 0 | 0 | 0
2019-05-27 | 293 | [6 empty] | 0 | 0 | 0
2019-05-28 | 273 | [6 empty] | 0 | 0 | 0
2019-05-29 | 266 | [6 empty] | 0 | 0 | 0
2019-05-30 | 259 | [6 empty] | 0 | 0 | 0
2019-05-31 | 269 | [6 empty] | 0 | 0 | 0
2019-06-01 | 281 | [6 empty] | 0 | 0 | 0
2019-06-02 | 311 | [6 empty] | 0 | 0 | 0
2019-06-03 | 291 | [6 empty] | 0 | 0 | 12
2019-06-04 | 258 | [6 empty] | 0 | 0 | 0
2019-06-05 | 240 | [6 empty] | 0 | 0 | 0
2019-06-06 | 248 | [6 empty] | 0 | 0 | 0
2019-06-07 | 235 | [6 empty] | 0 | 0 | 0
2019-06-08 | 211 | [6 empty] | 0 | 0 | 2
2019-06-09 | 223 | [6 empty] | 0 | 0 | 3
2019-06-10 | 233 | [6 empty] | 0 | 0 | 0
2019-06-11 | 245 | 10 | 70 | 2 | 38 | 7.3 | 3.4 | 0 | <1 | 0 | 10:00 | 2019-06-18 | 2019-06-18
2019-06-12 | 239 | [6 empty] | 0 | 0 | 0
2019-06-13 | 224 | [6 empty] | 0 | 0 | 0
2019-06-14 | 213 | [6 empty] | 0 | 0 | 0
2019-06-15 | 271 | [6 empty] | 0 | 0 | 0
2019-06-16 | 272 | [6 empty] | 0 | 0 | 0
2019-06-17 | 249 | [6 empty] | 0 | 0 | 13
2019-06-18 | 218 | [6 empty] | 0 | 0 | 0
2019-06-19 | 217 | [6 empty] | 0 | 0 | 0
2019-06-20 | 210 | [6 empty] | 0 | 0 | 0
2019-06-21 | 212 | [6 empty] | 0 | 0 | 0
2019-06-22 | 215 | [6 empty] | 0 | 0 | 0
2019-06-23 | 216 | [6 empty] | 0 | 0 | 0
2019-06-24 | 688 | [6 empty] | 0 | 0 | 0
2019-06-25 | 1454 | [6 empty] | 0 | 0 | 65 |  |  |  | Excessive inflow due to wet weather
2019-06-26 | 802 | [6 empty] | 0 | 0 | 26
2019-06-27 | 854 | [6 empty] | 0 | 0 | 18
2019-06-28 | 893 | [6 empty] | 0 | 0 | 10
2019-06-29 | 723 | [6 empty] | 0 | 0 | 5
2019-06-30 | 522 | [6 empty] | 0 | 0 | 0
2019-07-01 | 414 | [6 empty] | 0 | 0 | 0
2019-07-02 | 374 | [6 empty] | 0 | 0 | 0
2019-07-03 | 337 | [6 empty] | 0 | 0 | 34
2019-07-04 | 790 | [6 empty] | 0 | 0 | 0
2019-07-05 | 893 | [6 empty] | 0 | 0 | 15
2019-07-06 | 854 | [6 empty] | 0 | 0 | 0
2019-07-07 | 748 | [6 empty] | 0 | 0 | 0
2019-07-08 | 720 | [6 empty] | 0 | 0 | 11
2019-07-09 | 540 | 2 | 70 | 2 | 5 | 7 | 4.8 | 0 | 0 | 0 | 9:30 | 2019-07-22 | 2019-07-24
2019-07-10 | 438 | [6 empty] | 0 | 0 | 0
2019-07-11 | 378 | [6 empty] | 0 | 0 | 0
2019-07-12 | 347 | [6 empty] | 0 | 0 | 0
2019-07-13 | 329 | [6 empty] | 0 | 0 | 0
2019-07-14 | 311 | [6 empty] | 0 | 0 | 0
2019-07-15 | 283 | [6 empty] | 0 | 0 | 0
2019-07-16 | 278 | [6 empty] | 0 | 0 | 0
2019-07-17 | 271 | [6 empty] | 0 | 0 | 0
2019-07-18 | 258 | [6 empty] | 0 | 0 | 0
2019-07-19 | 272 | [6 empty] | 0 | 0 | 0
2019-07-20 | 266 | [6 empty] | 0 | 0 | 0
2019-07-21 | 275 | [6 empty] | 0 | 0 | 0
2019-07-22 | 261 | [6 empty] | 0 | 0 | 0
2019-07-23 | 260 | [6 empty] | 0 | 0 | 0
2019-07-24 | 257 | [6 empty] | 0 | 0 | 0
2019-07-25 | 248 | [6 empty] | 0 | 0 | 0
2019-07-26 | 243 | [6 empty] | 0 | 0 | 0
2019-07-27 | 267 | [6 empty] | 0 | 0 | 0
2019-07-28 | 261 | [6 empty] | 0 | 0 | 0
2019-07-29 | 254 | [6 empty] | 0 | 0 | 0
2019-07-30 | 235 | [6 empty] | 0 | 0 | 0
2019-07-31 | 269 | [6 empty] | 0 | 0 | 0
2019-08-01 | 255 | [6 empty] | 0 | 0 | 7
2019-08-02 | 242 | [6 empty] | 0 | 0 | 0
2019-08-03 | 261 | [6 empty] | 0 | 0 | 0
2019-08-04 | 260 | [6 empty] | 0 | 0 | 0
2019-08-05 | 246 | [6 empty] | 0 | 0 | 0
2019-08-06 | 230 | [6 empty] | 0 | 0 | 0
2019-08-07 | 221 | 4 | 52 | 2 | 7 | 6 | 5.4 | Zero Re-use | 0 | 0 | 9:00 | 2019-08-13 | 2019-08-13
2019-08-08 | 241 | [6 empty] | 0 | 0 | 0
2019-08-09 | 234 | [6 empty] | 0 | 0 | 0
2019-08-10 | 249 | [6 empty] | 0 | 0 | 0
2019-08-11 | 251 | [6 empty] | 0 | 0 | 0
2019-08-12 | 235 | [6 empty] | 0 | 0 | 0
2019-08-13 | 226 | [6 empty] | 0 | 0 | 0
2019-08-14 | 237 | [6 empty] | 0 | 0 | 0
2019-08-15 | 237 | [6 empty] | 0 | 0 | 0
2019-08-16 | 232 | [6 empty] | 0 | 0 | 0
2019-08-17 | 235 | [6 empty] | 0 | 0 | 0
2019-08-18 | 231 | [6 empty] | 0 | 0 | 0
2019-08-19 | 237 | [6 empty] | 0 | 0 | 0
2019-08-20 | 249 | [6 empty] | 0 | 0 | 0
2019-08-21 | 252 | [6 empty] | 0 | 0 | 0
2019-08-22 | 233 | [6 empty] | 0 | 0 | 0
2019-08-23 | 248 | [6 empty] | 0 | 0 | 0
2019-08-24 | 257 | [6 empty] | 0 | 0 | 0
2019-08-25 | 277 | [6 empty] | 0 | 0 | 0
2019-08-26 | 253 | [6 empty] | 0 | 0 | 0
2019-08-27 | 231 | [6 empty] | 0 | 0 | 0
2019-08-28 | 212 | [6 empty] | 0 | 0 | 0
2019-08-29 | 192 | [6 empty] | 0 | 0 | 0
2019-08-30 | 237 | [6 empty] | 0 | 0 | 5
2019-08-31 | 292 | [6 empty] | 0 | 0 | 13
MINIMUM | 166 | 2 | 31 | 2 | 5 | 5 | 1.6 | 0 | 0 | 0
AVERAGE | 301.5526 | 10.8 | 56.6 | 2.1 | 24.3 | 6.52 | 3.18 | 1.7225 | 0.49451 | 2.5096
MAXIMUM | 1481 | 17 | 70 | 3 | 61 | 9.1 | 5.4 | 394 | 90 | 70
TOTAL | 110066.688 | [6 empty] | 627 |  | 916
SAMPLE COUNT |  | 10
Non-compliant Results | 3 | 0 |  | 0 | 3 |  |  |  | 0

## 19-20
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 19/20
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2019-09-01 | 242 | [8 empty] | 0
2019-09-02 | 227 | [8 empty] | 0
2019-09-03 | 235 | [8 empty] | 0
2019-09-04 | 235 | [8 empty] | 1
2019-09-05 | 247 | [8 empty] | 0
2019-09-06 | 212 | [8 empty] | 0
2019-09-07 | 224 | [8 empty] | 0
2019-09-08 | 233 | [8 empty] | 0
2019-09-09 | 222 | [8 empty] | 0
2019-09-10 | 217 | [8 empty] | 0
2019-09-11 | 227 | [8 empty] | 0
2019-09-12 | 252 | [8 empty] | 0
2019-09-13 | 232 | [8 empty] | 0
2019-09-14 | 237 | [8 empty] | 0
2019-09-15 | 254 | [8 empty] | 0
2019-09-16 | 250 | [8 empty] | 0
2019-09-17 | 230 | [8 empty] | 0
2019-09-18 | 226 | [8 empty] | 0
2019-09-19 | 228 | [8 empty] | 0
2019-09-20 | 230 | [8 empty] | 0
2019-09-21 | 232 | [8 empty] | 0
2019-09-22 | 252 | [8 empty] | 0
2019-09-23 | 244 | [8 empty] | 0
2019-09-24 | 220 | [8 empty] | 0
2019-09-25 | 219 | [8 empty] | 0
2019-09-26 | 211 | [8 empty] | 0
2019-09-27 | 241 | [8 empty] | 0
2019-09-28 | 237 | [8 empty] | 0
2019-09-29 | 233 | [8 empty] | 0
2019-09-30 | 210 | [8 empty] | 0
2019-10-01 | 228 | 8 | 378 | 1 | 34 | 4.8 | 3.4 | 0 | 0 | 0 | 9:30 | 2019-10-17 | 2019-10-17
2019-10-02 | 232 | [8 empty] | 0
2019-10-03 | 240 | [8 empty] | 0
2019-10-04 | 255 | [8 empty] | 0
2019-10-05 | 218 | [8 empty] | 0
2019-10-06 | 191 | [8 empty] | 0
2019-10-07 | 209 | [8 empty] | 0
2019-10-08 | 200 | [8 empty] | 0
2019-10-09 | 224 | [8 empty] | 0
2019-10-10 | 209 | [8 empty] | 0
2019-10-11 | 205 | [8 empty] | 0
2019-10-12 | 222 | [8 empty] | 25
2019-10-13 | 215 | [8 empty] | 0
2019-10-14 | 204 | [8 empty] | 0
2019-10-15 | 198 | [8 empty] | 0
2019-10-16 | 220 | [8 empty] | 9
2019-10-17 | 196 | [8 empty] | 2
2019-10-18 | 201 | [8 empty] | 0
2019-10-19 | 207 | [8 empty] | 0
2019-10-20 | 199 | [8 empty] | 0
2019-10-21 | 209 | [8 empty] | 0
2019-10-22 | 201 | [8 empty] | 0
2019-10-23 | 200 | [8 empty] | 0
2019-10-24 | 199 | [8 empty] | 0
2019-10-25 | 190 | [8 empty] | 0
2019-10-26 | 195 | [8 empty] | 0
2019-10-27 | 198 | [8 empty] | 0
2019-10-28 | 191 | [8 empty] | 0
2019-10-29 | 196 | [8 empty] | 0
2019-10-30 | 198 | [8 empty] | 0
2019-10-31 | 193 | [8 empty] | 0
2019-11-01 | 195 | [8 empty] | 0
2019-11-02 | 209 | [8 empty] | 0
2019-11-03 | 213 | [8 empty] | 0
2019-11-04 | 196 | [8 empty] | 0
2019-11-05 | 208 | [8 empty] | 0
2019-11-06 | 206 | [8 empty] | 0
2019-11-07 | 191 | [8 empty] | 0
2019-11-08 | 189 | [8 empty] | 0
2019-11-09 | 194 | [8 empty] | 0
2019-11-10 | 199 | [8 empty] | 0
2019-11-11 | 188 | [8 empty] | 0
2019-11-12 | 184 | [8 empty] | 0
2019-11-13 | 199 | [8 empty] | 0
2019-11-14 | 204 | [8 empty] | 0
2019-11-15 | 196 | [8 empty] | 0
2019-11-16 | 205 | [8 empty] | 0
2019-11-17 | 199 | [8 empty] | 0
2019-11-18 | 204 | [8 empty] | 0
2019-11-19 | 199 | [8 empty] | 0
2019-11-20 | 198 | [8 empty] | 0
2019-11-21 | 195 | [8 empty] | 0
2019-11-22 | 197 | [8 empty] | 0
2019-11-23 | 201 | [8 empty] | 0
2019-11-24 | 209 | [8 empty] | 0
2019-11-25 | 203 | [8 empty] | 0
2019-11-26 | 194 | [8 empty] | 0
2019-11-27 | 184 | [8 empty] | 0
2019-11-28 | 202 | [8 empty] | 0
2019-11-29 | 183 | [8 empty] | 0
2019-11-30 | 230 | [8 empty] | 0
2019-12-01 | 243 | [8 empty] | 0
2019-12-02 | 213 | [8 empty] | 0
2019-12-03 | 197 | [8 empty] | 0
2019-12-04 | 202 | [8 empty] | 0
2019-12-05 | 203 | [8 empty] | 0
2019-12-06 | 196 | [8 empty] | 0
2019-12-07 | 199 | [8 empty] | 0
2019-12-08 | 198 | [8 empty] | 0
2019-12-09 | 199 | [8 empty] | 0
2019-12-10 | 196 | [8 empty] | 0
2019-12-11 | 191 | [8 empty] | 0
2019-12-12 | 202 | [8 empty] | 0
2019-12-13 | 182 | [8 empty] | 0
2019-12-14 | 212 | [8 empty] | 0
2019-12-15 | 203 | [8 empty] | 0
2019-12-16 | 191 | [8 empty] | 0
2019-12-17 | 198 | [8 empty] | 0
2019-12-18 | 138 | [8 empty] | 0
2019-12-19 | 287 | [8 empty] | 0
2019-12-20 | 193 | [8 empty] | 0
2019-12-21 | 187 | [8 empty] | 0
2019-12-22 | 194 | [8 empty] | 0
2019-12-23 | 195 | [8 empty] | 0
2019-12-24 | 365 | [8 empty] | 0
2019-12-25 | 202 | [8 empty] | 33
2019-12-26 | 208 | [8 empty] | 0
2019-12-27 | 212 | [8 empty] | 0
2019-12-28 | 208 | [8 empty] | 0
2019-12-29 | 203 | [8 empty] | 0
2019-12-30 | 207 | [8 empty] | 0
2019-12-31 | 191 | [8 empty] | 0
2020-01-01 | 197 | [8 empty] | 0
2020-01-02 | 201 | [8 empty] | 0
2020-01-03 | 205 | [8 empty] | 0
2020-01-04 | 179 | [8 empty] | 0
2020-01-05 | 199 | [8 empty] | 0
2020-01-06 | 188 | [8 empty] | 0
2020-01-07 | 255 | [8 empty] | 0
2020-01-08 | 298 | [8 empty] | 0
2020-01-09 | 282 | [8 empty] | 0
2020-01-10 | 272 | [8 empty] | 0
2020-01-11 | 288 | [8 empty] | 0
2020-01-12 | 293 | [8 empty] | 0
2020-01-13 | 280 | [8 empty] | 10
2020-01-14 | 235 | [8 empty] | 0
2020-01-15 | 263 | [8 empty] | 0
2020-01-16 | 267 | [8 empty] | 0
2020-01-17 | 231 | [8 empty] | 0
2020-01-18 | 1680 | [8 empty] | 55 |  |  |  | Heavy rainfall
2020-01-19 | 700 | [8 empty] | 0
2020-01-20 | 407 | [8 empty] | 125
2020-01-21 | 304 | 13 | 155 | 1 | 14 | 14 | 1.7 | 0 | 0 | 0 | 10:00 | 2020-02-11 | 2020-02-11
2020-01-22 | 264 | [8 empty] | 0
2020-01-23 | 280 | [8 empty] | 0
2020-01-24 | 257 | [8 empty] | 0
2020-01-25 | 274 | [8 empty] | 0
2020-01-26 | 265 | [8 empty] | 0
2020-01-27 | 312 | [8 empty] | 0
2020-01-28 | 307 | [8 empty] | 0
2020-01-29 | 242 | [8 empty] | 0
2020-01-30 | 279 | [8 empty] | 0
2020-01-31 | 287 | [8 empty] | 0
2020-02-01 | 264 | [8 empty] | 0
2020-02-02 | 275 | [8 empty] | 0
2020-02-03 | 239 | [8 empty] | 0
2020-02-04 | 377 | [8 empty] | 33
2020-02-05 | 265 | [8 empty] | 0
2020-02-06 | 1206 | [8 empty] | 8
2020-02-07 | 2135 | [8 empty] | 111 |  |  |  | Heavy rainfall
2020-02-08 | 1963 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-09 | 1388 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-10 | 1009 | [8 empty] | 55
2020-02-11 | 680 | [8 empty] | 0
2020-02-12 | 916 | [8 empty] | 62
2020-02-13 | 2032 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-14 | 1354 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-15 | 1387 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-16 | 666 | [8 empty] | 0
2020-02-17 | 580 | [8 empty] | 30
2020-02-18 | 541 | [8 empty] | 6
2020-02-19 | 558 | [8 empty] | 0
2020-02-20 | 425 | [8 empty] | 0
2020-02-21 | 369 | [8 empty] | 0
2020-02-22 | 312 | [8 empty] | 0
2020-02-23 | 380 | [8 empty] | 0
2020-02-24 | 436 | [8 empty] | 0
2020-02-25 | 452 | [8 empty] | 0
2020-02-26 | 598 | [8 empty] | 0
2020-02-27 | 656 | [8 empty] | 50
2020-02-28 | 1452 | [8 empty] | 0 |  |  |  | Heavy rainfall
2020-02-29 | 524 | [8 empty] | 0
2020-03-01 | 426 | [8 empty] | 0
2020-03-02 | 363 | [8 empty] | 0
2020-03-03 | 336 | [8 empty] | 0
2020-03-04 | 316 | [8 empty] | 8
2020-03-05 | 361 | [8 empty] | 0
2020-03-06 | 511 | [8 empty] | 0
2020-03-07 | 603 | [8 empty] | 0
2020-03-08 | 653 | [8 empty] | 8
2020-03-09 | 747 | [8 empty] | 0
2020-03-10 | 1659 | [8 empty] | 29 |  |  |  | Heavy rainfall
2020-03-11 | 760 | [8 empty] | 0
2020-03-12 | 722 | 11 | 179 | 1 | 16 | 6 | 2.5 | 0 | 0 | 0 | 10:00 | 2020-03-26 | 2020-03-26
2020-03-13 | 613 | [8 empty] | 0
2020-03-14 | 516 | [8 empty] | 0
2020-03-15 | 863 | [8 empty] | 0
2020-03-16 | 1205 | [8 empty] | 15
2020-03-17 | 539 | 9 | 248 | 1 | 12 | 6.5 | 2.5 | 0 | 0 | 0 | 9:00 | 2020-03-30 | 2020-03-30
2020-03-18 | 439 | [8 empty] | 0
2020-03-19 | 397 | [8 empty] | 0
2020-03-20 | 352 | [8 empty] | 0
2020-03-21 | 365 | [8 empty] | 0
2020-03-22 | 344 | [8 empty] | 0
2020-03-23 | 309 | [8 empty] | 0
2020-03-24 | 301 | [8 empty] | 0
2020-03-25 | 307 | [8 empty] | 6
2020-03-26 | 301 | [8 empty] | 0
2020-03-27 | 708 | [8 empty] | 37
2020-03-28 | 497 | [8 empty] | 0
2020-03-29 | 726 | [8 empty] | 0
2020-03-30 | 598 | [8 empty] | 0
2020-03-31 | 482 | [8 empty] | 0
2020-04-01 | 396 | [8 empty] | 0
2020-04-02 | 374 | [8 empty] | 0
2020-04-03 | 329 | [8 empty] | 0
2020-04-04 | 334 | [8 empty] | 0
2020-04-05 | 334 | [8 empty] | 0
2020-04-06 | 326 | [8 empty] | 0
2020-04-07 | 300 | [8 empty] | 0
2020-04-08 | 302 | [8 empty] | 7
2020-04-09 | 435 | [8 empty] | 0
2020-04-10 | 620 | [8 empty] | 21
2020-04-11 | 628 | [8 empty] | 11
2020-04-12 | 659 | [8 empty] | 0
2020-04-13 | 438 | [8 empty] | 0
2020-04-14 | 346 | 23 | 29 | 1 | 6 | 4.4 | 3.1 | 0 | 0 | 0 | 9:30 | 2020-04-22 | 2020-04-22
2020-04-15 | 321 | [8 empty] | 0
2020-04-16 | 316 | [8 empty] | 0
2020-04-17 | 299 | [8 empty] | 0
2020-04-18 | 296 | [8 empty] | 0
2020-04-19 | 307 | [8 empty] | 0
2020-04-20 | 299 | [8 empty] | 0
2020-04-21 | 280 | [8 empty] | 0
2020-04-22 | 280 | [8 empty] | 0
2020-04-23 | 272 | [8 empty] | 0
2020-04-24 | 284 | [8 empty] | 0
2020-04-25 | 284 | [8 empty] | 0
2020-04-26 | 284 | [8 empty] | 0
2020-04-27 | 267 | [8 empty] | 0
2020-04-28 | 337 | [8 empty] | 0
2020-04-29 | 302 | [8 empty] | 0
2020-04-30 | 290 | [8 empty] | 12
2020-05-01 | 280 | [8 empty] | 0
2020-05-02 | 288 | [8 empty] | 0
2020-05-03 | 281 | [8 empty] | 0
2020-05-04 | 266 | [8 empty] | 0
2020-05-05 | 264 | [8 empty] | 0
2020-05-06 | 284 | [8 empty] | 0
2020-05-07 | 266 | [8 empty] | 0
2020-05-08 | 275.5 | [8 empty] | 0
2020-05-09 | 275.5 | [8 empty] | 0
2020-05-10 | 285 | [8 empty] | 0
2020-05-11 | 271 | [8 empty] | 0
2020-05-12 | 258 | 14 | 28 | 1 | 9 | 4.7 | 3.8 | 0 | 0 | 0 | 8:00 | 2020-05-19 | 2020-05-20
2020-05-13 | 276 | [8 empty] | 0
2020-05-14 | 264 | [8 empty] | 0
2020-05-15 | 274 | [8 empty] | 0
2020-05-16 | 289 | [8 empty] | 0
2020-05-17 | 372 | [8 empty] | 0
2020-05-18 | 378 | [8 empty] | 23
2020-05-19 | 296 | [8 empty] | 0
2020-05-20 | 286 | [8 empty] | 3
2020-05-21 | 292 | [8 empty] | 0
2020-05-22 | 286 | [8 empty] | 0
2020-05-23 | 274 | [8 empty] | 0
2020-05-24 | 285 | [8 empty] | 0
2020-05-25 | 260 | [8 empty] | 0
2020-05-26 | 258 | [8 empty] | 0
2020-05-27 | 246 | [8 empty] | 0
2020-05-28 | 261 | [8 empty] | 0
2020-05-29 | 253 | [8 empty] | 0
2020-05-30 | 290 | [8 empty] | 0
2020-05-31 | 281 | [8 empty] | 0
2020-06-01 | 272 | [8 empty] | 0
2020-06-02 | 263 | [8 empty] | 0
2020-06-03 | 244 | [8 empty] | 0
2020-06-04 | 234 | [8 empty] | 0
2020-06-05 | 236 | [8 empty] | 0
2020-06-06 | 252 | [8 empty] | 0
2020-06-07 | 237 | [8 empty] | 0
2020-06-08 | 264 | [8 empty] | 18
2020-06-09 | 239 | [8 empty] | 0
2020-06-10 | 261 | 13 | 142 | 1 | 17 | 7.3 | 3.2 | 0 | 0 | 0 | 13:00 | 2020-06-22 | 2020-06-30
2020-06-11 | 643 | [8 empty] | 41
2020-06-12 | 396 | [8 empty] | 0
2020-06-13 | 342 | [8 empty] | 0
2020-06-14 | 591 | [8 empty] | 0
2020-06-15 | 475 | [8 empty] | 21
2020-06-16 | 385 | [8 empty] | 0
2020-06-17 | 329 | [8 empty] | 4
2020-06-18 | 366 | [8 empty] | 0
2020-06-19 | 473 | [8 empty] | 0
2020-06-20 | 462 | [8 empty] | 0
2020-06-21 | 433 | [8 empty] | 0
2020-06-22 | 429 | [8 empty] | 10
2020-06-23 | 339 | [8 empty] | 0
2020-06-24 | 310 | [8 empty] | 0
2020-06-25 | 301 | [8 empty] | 0
2020-06-26 | 275 | [8 empty] | 0
2020-06-27 | 283 | [8 empty] | 0
2020-06-28 | 302 | [8 empty] | 0
2020-06-29 | 283 | [8 empty] | 10
2020-06-30 | 256 | [8 empty] | 2
2020-07-01 | 262 | [8 empty] | 0
2020-07-02 | 248 | [8 empty] | 0
2020-07-03 | 246 | [8 empty] | 0
2020-07-04 | 258 | [8 empty] | 0
2020-07-05 | 240 | [8 empty] | 0
2020-07-06 | 241 | [8 empty] | 0
2020-07-07 | 232 | [8 empty] | 0
2020-07-08 | 289 | 9 | 291 | 1 | 15 | 9.1 | 3.2 | 0 | 0 | 0 | 9:00 | 2020-07-15 | 2020-07-15
2020-07-09 | 261 | [8 empty] | 15
2020-07-10 | 272 | [8 empty] | 0
2020-07-11 | 277 | [8 empty] | 0
2020-07-12 | 253 | [8 empty] | 0
2020-07-13 | 263 | [8 empty] | 0
2020-07-14 | 247 | [8 empty] | 0
2020-07-15 | 238 | [8 empty] | 0
2020-07-16 | 236 | [8 empty] | 0
2020-07-17 | 234 | [8 empty] | 0
2020-07-18 | 238 | [8 empty] | 0
2020-07-19 | 248 | [8 empty] | 0
2020-07-20 | 247 | [8 empty] | 0
2020-07-21 | 241 | [8 empty] | 0
2020-07-22 | 220 | [8 empty] | 0
2020-07-23 | 231 | [8 empty] | 0
2020-07-24 | 914 | [8 empty] | 32
2020-07-25 | 813 | [8 empty] | 32
2020-07-26 | 1817 | [8 empty] | 0 |  |  |  | heavy rainfall
2020-07-27 | 956 | [8 empty] | 43
2020-07-28 | 557 | [8 empty] | 0
2020-07-29 | 456 | [8 empty] | 0
2020-07-30 | 395 | [8 empty] | 0
2020-07-31 | 358 | [8 empty] | 0
2020-08-01 | 344 | [8 empty] | 0
2020-08-02 | 341 | [8 empty] | 0
2020-08-03 | 331 | [8 empty] | 0
2020-08-04 | 314 | [8 empty] | 0
2020-08-05 | 300 | 9 | 101 | 1 | 12 | 8.1 | 3.4 | 0 | 0 | 0 | 11:30 | 2020-08-18 | 2020-08-18
2020-08-06 | 291 | [8 empty] | 0
2020-08-07 | 293 | [8 empty] | 0
2020-08-08 | 311 | [8 empty] | 0
2020-08-09 | 308 | [8 empty] | 0
2020-08-10 | 271 | [8 empty] | 0
2020-08-11 | 268 | [8 empty] | 0
2020-08-12 | 265 | [8 empty] | 0
2020-08-13 | 265 | [8 empty] | 0
2020-08-14 | 269 | [8 empty] | 0
2020-08-15 | 269 | [8 empty] | 0
2020-08-16 | 411 | [8 empty] | 0
2020-08-17 | 326 | [8 empty] | 0
2020-08-18 | 290 | [8 empty] | 0
2020-08-19 | 277 | [8 empty] | 0
2020-08-20 | 277 | [8 empty] | 0
2020-08-21 | 263 | [8 empty] | 0
2020-08-22 | 268 | [8 empty] | 0
2020-08-23 | 268 | [8 empty] | 0
2020-08-24 | 258 | [8 empty] | 0
2020-08-25 | 260 | [8 empty] | 0
2020-08-26 | 248 | [8 empty] | 0
2020-08-27 | 247 | [8 empty] | 0
2020-08-28 | 245 | [8 empty] | 0
2020-08-29 | 256 | [8 empty] | 0
2020-08-30 | 271 | [8 empty] | 0
2020-08-31 | 247 | [8 empty] | 0
MINIMUM | 138 | 8 | 28 | 1 | 6 | 4.4 | 1.7 | 0 | 0 | 0
AVERAGE | 346.4727 | 12.1111 | 172.3333 | 1 | 15 | 7.2111 | 2.9778 | 0 | 0 | 2.7951
MAXIMUM | 2135 | 23 | 378 | 1 | 34 | 14 | 3.8 | 0 | 0 | 125
TOTAL | 126809 | [6 empty] | 0 |  | 1023
SAMPLE COUNT |  | 9
Non-compliant Results | 10 | 1 |  | 0 | 1 |  |  |  | 0

## 20-21
Monthly Effluent Quality & Daily Volume Monitoring
Richmond Valley Council - Corner Walker Street & Graham Place, (Locked Bag 10) Casino NSW 2470
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 20/21
EPA Licence Number: 351 - Box Ridge Road Coraki
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Sample Collected By | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2020-09-01 | 245 | [6 empty] | 0 |  | 0
2020-09-02 | 370 | 5 | <1 | <2 | 23 | 5.9 | 1.5 |  |  | 0 | 10:00 | Craig Smith | 2020-09-14 | 2020-09-14
2020-09-03 | 265 | [6 empty] | 0 |  | 0
2020-09-04 | 243 | [6 empty] | 0 |  | 0
2020-09-05 | 258 | [6 empty] | 0 |  | 0
2020-09-06 | 241 | [6 empty] | 0 |  | 0
2020-09-07 | 238 | [6 empty] | 0 |  | 0
2020-09-08 | 283 | [6 empty] | 0 |  | 0
2020-09-09 | 251 | [6 empty] | 0 |  | 0
2020-09-10 | 327 | [6 empty] | 0 |  | 0
2020-09-11 | 328 | [6 empty] | 0 |  | 0
2020-09-12 | 277 | [6 empty] | 0 |  | 0
2020-09-13 | 269 | [6 empty] | 0 |  | 0
2020-09-14 | 251 | [6 empty] | 0 |  | 0
2020-09-15 | 238 | [6 empty] | 0 |  | 0
2020-09-16 | 243 | [6 empty] | 0 |  | 0
2020-09-17 | 242 | [6 empty] | 0 |  | 0
2020-09-18 | 225 | [6 empty] | 0 |  | 0
2020-09-19 | 230 | [6 empty] | 0 |  | 0
2020-09-20 | 235 | [6 empty] | 0 |  | 0
2020-09-21 | 231 | [6 empty] | 0 |  | 0
2020-09-22 | 240 | [6 empty] | 0 |  | 0
2020-09-23 | 224 | [6 empty] | 0 |  | 0
2020-09-24 | 233 | [6 empty] | 0 |  | 0
2020-09-25 | 227 | [6 empty] | 0 |  | 0
2020-09-26 | 219 | [6 empty] | 0 |  | 0
2020-09-27 | 226 | [6 empty] | 0 |  | 0
2020-09-28 | 224 | [6 empty] | 0 |  | 0
2020-09-29 | 215 | [6 empty] | 0 |  | 0
2020-09-30 | 215 | [6 empty] | 0 |  | 0
2020-10-01 | 215 | [6 empty] | 0 |  | 0
2020-10-02 | 212 | [6 empty] | 0 |  | 0
2020-10-03 | 209 | [6 empty] | 0 |  | 0
2020-10-04 | 212 | [6 empty] | 0 |  | 0
2020-10-05 | 222 | [6 empty] | 0 |  | 0
2020-10-06 | 203 | 5 | <1 | <2 | 24 | 3.7 | 1.3 | 0 |  | 0 | 10:00 | Criag Smith | 2020-10-16 | 2020-10-16
2020-10-07 | 204 | [6 empty] | 0 |  | 0
2020-10-08 | 206 | [6 empty] | 0 |  | 0
2020-10-09 | 201 | [6 empty] | 0 |  | 0
2020-10-10 | 219 | [6 empty] | 0 |  | 0
2020-10-11 | 215 | [6 empty] | 0 |  | 0
2020-10-12 | 219 | [6 empty] | 0 |  | 0
2020-10-13 | 218 | [6 empty] | 0 |  | 0
2020-10-14 | 204 | [6 empty] | 0 |  | 0
2020-10-15 | 219 | [6 empty] | 0 |  | 0
2020-10-16 | 208 | [6 empty] | 0 |  | 0
2020-10-17 | 232 | [6 empty] | 0 |  | 0
2020-10-18 | 214 | [6 empty] | 0 |  | 0
2020-10-19 | 229 | [6 empty] | 0 |  | 13
2020-10-20 | 200 | [6 empty] | 0 |  | 0
2020-10-21 | 202 | [6 empty] | 0 |  | 0
2020-10-22 | 197 | [6 empty] | 0 |  | 0
2020-10-23 | 194 | [6 empty] | 0 |  | 0
2020-10-24 | 196 | [6 empty] | 0 |  | 0
2020-10-25 | 250 | [6 empty] | 0 |  | 0
2020-10-26 | 276 | [6 empty] | 0 |  | 42
2020-10-27 | 239 | [6 empty] | 0 |  | 9
2020-10-28 | 338 | [6 empty] | 0 |  | 41
2020-10-29 | 594 | [6 empty] | 0 |  | 22
2020-10-30 | 363 | [6 empty] | 0 |  | 0
2020-10-31 | 272 | [6 empty] | 0 |  | 0
2020-11-01 | 253 | [6 empty] | 0 |  | 0
2020-11-02 | 235 | [6 empty] | 0 |  | 0
2020-11-03 | 239 | [6 empty] | 0 |  | 0
2020-11-04 | 237 | [6 empty] | 0 |  | 0
2020-11-05 | 240 | [6 empty] | 0 |  | 0
2020-11-06 | 225 | [6 empty] | 0 |  | 2
2020-11-07 | 228 | [6 empty] | 0 |  | 0
2020-11-08 | 223 | [6 empty] | 0 |  | 0
2020-11-09 | 232 | [6 empty] | 0 |  | 0
2020-11-10 | 222 | 15 | 36 | <2 | 59 | 9.3 | 1.6 | 0 |  | 0 | 9:00 | Harley Hyde | 2020-11-25 | 2020-11-25
2020-11-11 | 241 | [6 empty] | 0 |  | 0
2020-11-12 | 228 | [6 empty] | 0 |  | 0
2020-11-13 | 215 | [6 empty] | 0 |  | 0
2020-11-14 | 233 | [6 empty] | 0 |  | 0
2020-11-15 | 221 | [6 empty] | 0 |  | 0
2020-11-16 | 219 | [6 empty] | 0 |  | 0
2020-11-17 | 221 | [6 empty] | 0 |  | 0
2020-11-18 | 197 | [6 empty] | 0 |  | 0
2020-11-19 | 199 | [6 empty] | 0 |  | 0
2020-11-20 | 223 | [6 empty] | 0 |  | 0
2020-11-21 | 217 | [6 empty] | 0 |  | 0
2020-11-22 | 216 | [6 empty] | 0 |  | 0
2020-11-23 | 222 | [6 empty] | 0 |  | 0
2020-11-24 | 195 | [6 empty] | 0 |  | 0
2020-11-25 | 202 | [6 empty] | 0 |  | 0
2020-11-26 | 204 | [6 empty] | 0 |  | 0
2020-11-27 | 213 | [6 empty] | 0 |  | 0
2020-11-28 | 213 | [6 empty] | 0 |  | 0
2020-11-29 | 232 | [6 empty] | 0 |  | 0
2020-11-30 | 205 | [6 empty] | 0 |  | 0
2020-12-01 | 207 | [6 empty] | 0 |  | 0
2020-12-02 | 215 | [6 empty] | 0 |  | 0
2020-12-03 | 202 | [6 empty] | 0 |  | 0
2020-12-04 | 198 | [6 empty] | 0 |  | 0
2020-12-05 | 211 | [6 empty] | 0 |  | 0
2020-12-06 | 214 | [6 empty] | 0 |  | 0
2020-12-07 | 199 | [6 empty] | 0 |  | 0
2020-12-08 | 201 | [6 empty] | 0 |  | 0
2020-12-09 | 200 | 23 | 214 | 1 | 15 | 6.9 | 1.8 | 0 |  | 0 | 9:00 | Craig Smith | 23.12.2021 | 23.12.2021
2020-12-10 | 211 | [6 empty] | 0 |  | 0
2020-12-11 | 299 | [6 empty] | 0 |  | 0
2020-12-12 | 893 | [6 empty] | 0 |  | 40
2020-12-13 | 711 | [6 empty] | 0 |  | 0
2020-12-14 | 1606 | [6 empty] | 0 |  | 65 |  |  |  |  | heavy rainfall
2020-12-15 | 1991 | [6 empty] | 0 |  | 0 |  |  |  |  | heavy rainfall
2020-12-16 | 1468 | [6 empty] | 0 |  | 85 |  |  |  |  | heavy rainfall
2020-12-17 | 2400 | [6 empty] | 0 |  | 205 |  |  |  |  | heavy rainfall
2020-12-18 | 431 | [6 empty] | 0 |  | 4
2020-12-19 | 739 | [6 empty] | 0 |  | 0
2020-12-20 | 906 | [6 empty] | 0 |  | 0
2020-12-21 | 881 | [6 empty] | 0 |  | 42
2020-12-22 | 615 | [6 empty] | 0 |  | 0
2020-12-23 | 526 | [6 empty] | 0 |  | 0
2020-12-24 | 425 | [6 empty] | 0 |  | 0
2020-12-25 | 526 | [6 empty] | 0 |  | 0
2020-12-26 | 438 | [6 empty] | 0 |  | 0
2020-12-27 | 389 | [6 empty] | 0 |  | 0
2020-12-28 | 353 | [6 empty] | 0 |  | 0
2020-12-29 | 434 | [6 empty] | 0 |  | 0
2020-12-30 | 1247 | [6 empty] | 0 |  | 0
2020-12-31 | 611 | [6 empty] | 0 |  | 45
2021-01-01 | 555 | [6 empty] | 0 |  | 0
2021-01-02 | 749 | [6 empty] | 0 |  | 8
2021-01-03 | 572 | [6 empty] | 0 |  | 3
2021-01-04 | 451 | [6 empty] | 0 |  | 0
2021-01-05 | 429 | [6 empty] | 0 |  | 0
2021-01-06 | 495 | [6 empty] | 0 |  | 22
2021-01-07 | 839 | [6 empty] | 0 |  | 0
2021-01-08 | 923 | [6 empty] | 0 |  | 0
2021-01-09 | 869 | [6 empty] | 0 |  | 0
2021-01-10 | 589 | [6 empty] | 0 |  | 0
2021-01-11 | 607 | [6 empty] | 0 |  | 0
2021-01-12 | 412 | 14 | 1 | 1 | 19 | 5 | 1.4 | 0 |  | 0 | 09:00:00AM | Craig Smith | 23.12.2021 | 23.12.2021
2021-01-13 | 369 | [6 empty] | 0 |  | 0
2021-01-14 | 336 | [6 empty] | 0 |  | 0
2021-01-15 | 330 | [6 empty] | 0 |  | 0
2021-01-16 | 351 | [6 empty] | 0 |  | 0
2021-01-17 | 314 | [6 empty] | 0 |  | 0
2021-01-18 | 426 | [6 empty] | 0 |  | 40
2021-01-19 | 404 | [6 empty] | 0 |  | 0
2021-01-20 | 341 | [6 empty] | 0 |  | 5
2021-01-21 | 347 | [6 empty] | 0 |  | 0
2021-01-22 | 336 | [6 empty] | 0 |  | 0
2021-01-23 | 345 | [6 empty] | 0 |  | 0
2021-01-24 | 326 | [6 empty] | 0 |  | 0
2021-01-25 | 301 | [6 empty] | 0 |  | 0
2021-01-26 | 291 | [6 empty] | 0 |  | 0
2021-01-27 | 298 | [6 empty] | 0 |  | 0
2021-01-28 | 287 | [6 empty] | 0 |  | 0
2021-01-29 | 283 | [6 empty] | 0 |  | 0
2021-01-30 | 276 | [6 empty] | 0 |  | 0
2021-01-31 | 288 | [6 empty] | 0 |  | 0
2021-02-01 | 265 | [6 empty] | 0 |  | 0
2021-02-02 | 270 | [6 empty] | 0 |  | 0
2021-02-03 | 298 | [6 empty] | 0 |  | 0
2021-02-04 | 262 | [6 empty] | 0 |  | 0
2021-02-05 | 260 | 14 | 1 | 1 | 59 | 5 | 1.3 | 0 |  | 0 | 09:30:00AM | Harley Hyde | 24.02.2021 | 24.02.2021
2021-02-06 | 267 | [6 empty] | 0 |  | 0
2021-02-07 | 268 | [6 empty] | 0 |  | 0
2021-02-08 | 236 | [6 empty] | 0 |  | 0
2021-02-09 | 249 | [6 empty] | 0 |  | 0
2021-02-10 | 243 | [6 empty] | 0 |  | 5
2021-02-11 | 248 | [6 empty] | 0 |  | 5
2021-02-12 | 254 | [6 empty] | 0 |  | 0
2021-02-13 | 261 | [6 empty] | 0 |  | 0
2021-02-14 | 69 | [6 empty] | 0 |  | 0
2021-02-15 | 268 | [6 empty] | 0 |  | 0
2021-02-16 | 448 | [6 empty] | 0 |  | 0
2021-02-17 | 550 | [6 empty] | 0 |  | 21
2021-02-18 | 1402 | [6 empty] | 0 |  | 23
2021-02-19 | 2267 | [6 empty] | 0 |  | 22
2021-02-20 | 832 | [6 empty] | 0 |  | 20
2021-02-21 | 684 | [6 empty] | 0 |  | 30
2021-02-22 | 686 | [6 empty] | 0 |  | 0
2021-02-23 | 707 | [6 empty] | 0 |  | 0
2021-02-24 | 907 | [6 empty] | 0 |  | 0
2021-02-25 | 1527 | [6 empty] | 0 |  | 0
2021-02-26 | 1566 | [6 empty] | 0 |  | 40
2021-02-27 | 855 | [6 empty] | 0 |  | 0
2021-02-28 | 531 | [6 empty] | 0 |  | 0
2021-03-01 | 546 | [6 empty] | 0 |  | 0
2021-03-02 | 511 | [6 empty] | 0 |  | 0
2021-03-03 | 473 | 11 | 11 | <2 | 9.6 | 4.4 | 1.4 | 0 |  | 0 | 08:00:00AM | Craig Smith | 23.03.2021 | 23.03.2021
2021-03-04 | 1257 | [6 empty] | 0 |  | 0
2021-03-05 | 684 | [6 empty] | 0 |  | 0
2021-03-06 | 1287 | [6 empty] | 0 |  | 0
2021-03-07 | 509 | [6 empty] | 0 |  | 0
2021-03-08 | 526 | [6 empty] | 0 |  | 20
2021-03-09 | 1374 | [6 empty] | 0 |  | 38
2021-03-10 | 1512 | [6 empty] | 0 |  | 0
2021-03-11 | 1570 | [6 empty] | 0 |  | 0
2021-03-12 | 1979 | [6 empty] | 0 |  | 0
2021-03-13 | 1190 | [6 empty] | 0 |  | 0
2021-03-14 | 675 | [6 empty] | 0 |  | 0
2021-03-15 | 715 | [6 empty] | 0 |  | 0
2021-03-16 | 1129 | [6 empty] | 0 |  | 0
2021-03-17 | 1119 | [6 empty] | 0 |  | 24
2021-03-18 | 1404 | [6 empty] | 0 |  | 6
2021-03-19 | 957 | [6 empty] | 0 |  | 0
2021-03-20 | 986 | [6 empty] | 0 |  | 0
2021-03-21 | 1757 | [6 empty] | 0 |  | 0
2021-03-22 | 2112 | [6 empty] | 0 |  | 0
2021-03-23 | 2067 | [6 empty] | 0 |  | 0
2021-03-24 | 1821 | [6 empty] | 0 |  | 0
2021-03-25 | 1873 | [6 empty] | 0 |  | 0
2021-03-26 | 1203 | [6 empty] | 0 |  | 0
2021-03-27 | 899 | [6 empty] | 0 |  | 0
2021-03-28 | 573 | [6 empty] | 0 |  | 0
2021-03-29 | 551 | [6 empty] | 0 |  | 0
2021-03-30 | 577 | [6 empty] | 0 |  | 0
2021-03-31 | 511 | [6 empty] | 0 |  | 0
2021-04-01 | 829 | [6 empty] | 0 |  | 0
2021-04-02 | 922 | [6 empty] | 0 |  | 0
2021-04-03 | 950 | [6 empty] | 0 |  | 0
2021-04-04 | 737 | [6 empty] | 0 |  | 0
2021-04-05 | 1384 | [6 empty] | 0 |  | 0
2021-04-06 | 2045 | [6 empty] | 0 |  | 0
2021-04-07 | 2105 | [6 empty] | 0 |  | 0
2021-04-08 | 2107 | [6 empty] | 0 |  | 0
2021-04-09 | 1849 | [6 empty] | 0 |  | 0
2021-04-10 | 1331 | [6 empty] | 0 |  | 0
2021-04-11 | 720 | [6 empty] | 0 |  | 0
2021-04-12 | 720 | [6 empty] | 0 |  | 0
2021-04-13 | 610 | [6 empty] | 0 |  | 0
2021-04-14 | 550 | 8 | 727 | <2 | 22 | 4 | 1.8 | 0 |  | 0 | 08:00:00AM | Harley Hyde | 29.04.2021 | 30.04.2021
2021-04-15 | 572 | [6 empty] | 0 |  | 0
2021-04-16 | 486 | [6 empty] | 0 |  | 0
2021-04-17 | 460 | [6 empty] | 0 |  | 0
2021-04-18 | 471 | [6 empty] | 0 |  | 0
2021-04-19 | 438 | [6 empty] | 0 |  | 0
2021-04-20 | 418 | [6 empty] | 0 |  | 0
2021-04-21 | 386 | [6 empty] | 0 |  | 0
2021-04-22 | 372 | [6 empty] | 0 |  | 0
2021-04-23 | 364 | [6 empty] | 0 |  | 0
2021-04-24 | 84 | [6 empty] | 0 |  | 0
2021-04-25 | 351 | [6 empty] | 0 |  | 0
2021-04-26 | 339 | [6 empty] | 0 |  | 0
2021-04-27 | 340 | [6 empty] | 0 |  | 0
2021-04-28 | 363 | [6 empty] | 0 |  | 0
2021-04-29 | 370 | [6 empty] | 0 |  | 0
2021-04-30 | 551 | [6 empty] | 0 |  | 0
2021-05-01 | 762 | [6 empty] | 0 |  | 0
2021-05-02 | 639 | [6 empty] | 0 |  | 0
2021-05-03 | 639 | [6 empty] | 0 |  | 0
2021-05-04 | 466 | [6 empty] | 0 |  | 0
2021-05-05 | 635 | [6 empty] | 0 |  | 0
2021-05-06 | 806 | [6 empty] | 0 |  | 0
2021-05-07 | 1188 | [6 empty] | 0 |  | 0
2021-05-08 | 669 | [6 empty] | 0 |  | 0
2021-05-09 | 551 | [6 empty] | 0 |  | 0
2021-05-10 | 524 | [6 empty] | 0 |  | 0
2021-05-11 | 467 | [6 empty] | 0 |  | 0
2021-05-12 | 445 | 7 | 43 | <2 | 23 | 7.3 | 2.4 | 0 |  | 0 | 08:20:00AM | Harley Hyde | 27.05.2021 | 04.06.2021
2021-05-13 | 446 | [6 empty] | 0 |  | 0
2021-05-14 | 411 | [6 empty] | 0 |  | 0
2021-05-15 | 391 | [6 empty] | 0 |  | 0
2021-05-16 | 390 | [6 empty] | 0 |  | 0
2021-05-17 | 356 | [6 empty] | 0 |  | 0
2021-05-18 | 333 | [6 empty] | 0 |  | 0
2021-05-19 | 343 | [6 empty] | 0 |  | 0
2021-05-20 | 349 | [6 empty] | 0 |  | 0
2021-05-21 | 333 | [6 empty] | 0 |  | 0
2021-05-22 | 327 | [6 empty] | 0 |  | 0
2021-05-23 | 86? | [6 empty] | 0 |  | 0
2021-05-24 | 598 | [6 empty] | 0 |  | 0
2021-05-25 | 325 | [6 empty] | 0 |  | 0
2021-05-26 | 328 | [6 empty] | 0 |  | 0
2021-05-27 | 309 | [6 empty] | 0 |  | 0
2021-05-28 | 311 | [6 empty] | 0 |  | 0
2021-05-29 | 307 | [6 empty] | 0 |  | 0
2021-05-30 | 305 | [6 empty] | 0 |  | 0
2021-05-31 | 304 | [6 empty] | 0 |  | 0
2021-06-01 | 297 | [6 empty] | 0 |  | 0
2021-06-02 | 300 | [6 empty] | 0 |  | 0
2021-06-03 | 299 | [6 empty] | 0 |  | 0
2021-06-04 | 305 | [6 empty] | 0 |  | 0
2021-06-05 | 299 | [6 empty] | 0 |  | 0
2021-06-06 | 298 | [6 empty] | 0 |  | 0
2021-06-07 | 302 | [6 empty] | 0 |  | 0
2021-06-08 | 286 | [6 empty] | 0 |  | 0
2021-06-09 | 291 | 6 | 236 | <2 | 25 | 5.6 | 2 | 0 |  | 0 | 8:00 | Harley Hyde | 25.06.2021 | 23.07.2021
2021-06-10 | 294 | [6 empty] | 0 |  | 0
2021-06-11 | 287 | [6 empty] | 0 |  | 0
2021-06-12 | 290 | [6 empty] | 0 |  | 0
2021-06-13 | 274 | [6 empty] | 0 |  | 0
2021-06-14 | 282 | [6 empty] | 0 |  | 0
2021-06-15 | 262 | [6 empty] | 0 |  | 0
2021-06-16 | 264 | [6 empty] | 0 |  | 0
2021-06-17 | 281 | [6 empty] | 0 |  | 0
2021-06-18 | 257 | [6 empty] | 0 |  | 0
2021-06-19 | 260 | [6 empty] | 0 |  | 0
2021-06-20 | 280 | [6 empty] | 0 |  | 0
2021-06-21 | 255 | [6 empty] | 0 |  | 0
2021-06-22 | 252 | [6 empty] | 0 |  | 0
2021-06-23 | 178 | [6 empty] | 0 |  | 0
2021-06-24 | 248 | [6 empty] | 0 |  | 0
2021-06-25 | 250 | [6 empty] | 0 |  | 0
2021-06-26 | 272 | [6 empty] | 0 |  | 0
2021-06-27 | 287 | [6 empty] | 0 |  | 0
2021-06-28 | 268 | [6 empty] | 0 |  | 0
2021-06-29 | 294 | [6 empty] | 0 |  | 0
2021-06-30 | 285 | [6 empty] | 0 |  | 13
2021-07-01 | 326 | [6 empty] | 0 |  | 20
2021-07-02 | 487 | [6 empty] | 0 |  | 0
2021-07-03 | 375 | [6 empty] | 0 |  | 0
2021-07-04 | 351 | [6 empty] | 0 |  | 0
2021-07-05 | 308 | [6 empty] | 0 |  | 0
2021-07-06 | 290 | [6 empty] | 0 |  | 0
2021-07-07 | 286 | [6 empty] | 0 |  | 0
2021-07-08 | 272 | [6 empty] | 0 |  | 0
2021-07-09 | 437 | [6 empty] | 0 |  | 0
2021-07-10 | 382 | [6 empty] | 0 |  | 0
2021-07-11 | 329 | [6 empty] | 0 |  | 0
2021-07-12 | 303 | [6 empty] | 0 |  | 0
2021-07-13 | 287 | [6 empty] | 0 |  | 0
2021-07-14 | 285 | 7 | 35 | <2 | 19 | 5.9 | 3 | 0 |  | 0 | 10.00am | Harley Hyde | 29.07.2021 | 13.08.2021
2021-07-15 | 275 | [6 empty] | 0 |  | 0
2021-07-16 | 282 | [6 empty] | 0 |  | 0
2021-07-17 | 294 | [6 empty] | 0 |  | 0
2021-07-18 | 280 | [6 empty] | 0 |  | 0
2021-07-19 | 257 | [6 empty] | 0 |  | 0
2021-07-20 | 266 | [6 empty] | 0 |  | 0
2021-07-21 | 271 | [6 empty] | 0 |  | 0
2021-07-22 | 267 | [6 empty] | 0 |  | 0
2021-07-23 | 241 | [6 empty] | 0 |  | 0
2021-07-24 | 270 | [6 empty] | 0 |  | 0
2021-07-25 | 275 | [6 empty] | 0 |  | 0
2021-07-26 | 251 | [6 empty] | 0 |  | 0
2021-07-27 | 257 | [6 empty] | 0 |  | 0
2021-07-28 | 266 | [6 empty] | 0 |  | 0
2021-07-29 | 254 | [6 empty] | 0 |  | 0
2021-07-30 | 260 | [6 empty] | 0 |  | 0
2021-07-31 | 265 | [6 empty] | 0 |  | 0
2021-08-01 | 261 | [6 empty] | 0 |  | 0
2021-08-02 | 236 | [6 empty] | 0 |  | 0
2021-08-03 | 247 | [6 empty] | 0 |  | 0
2021-08-04 | 243 | 4 | 113 | <2 | 7 | 7.8 | 4.2 | 0 |  | 0 | 8.00am | Craig Smith | 12.08.2021 | 13.08.2021
2021-08-05 | 244 | [6 empty] | 0 |  | 0
2021-08-06 | 244 | [6 empty] | 0 |  | 0
2021-08-07 | 239 | [6 empty] | 0 |  | 0
2021-08-08 | 273 | [6 empty] | 0 |  | 0
2021-08-09 | 256 | [6 empty] | 0 |  | 0
2021-08-10 | 258 | [6 empty] | 0 |  | 0
2021-08-11 | 245 | [6 empty] | 0 |  | 0
2021-08-12 | 263 | [6 empty] | 0 |  | 0
2021-08-13 | 245 | [6 empty] | 0 |  | 0
2021-08-14 | 261 | [6 empty] | 0 |  | 0
2021-08-15 | 256 | [6 empty] | 0 |  | 0
2021-08-16 | 254 | [6 empty] | 0 |  | 0
2021-08-17 | 243 | [6 empty] | 0 |  | 0
2021-08-18 | 234 | [6 empty] | 0 |  | 0
2021-08-19 | 246 | [6 empty] | 0 |  | 0
2021-08-20 | 236 | [6 empty] | 0 |  | 0
2021-08-21 | 251 | [6 empty] | 0 |  | 0
2021-08-22 | 243 | [6 empty] | 0 |  | 0
2021-08-23 | 233 | [6 empty] | 0 |  | 0
2021-08-24 | 238 | [6 empty] | 0 |  | 0
2021-08-25 | 235 | [6 empty] | 0 |  | 0
2021-08-26 | 230 | [6 empty] | 0 |  | 0
2021-08-27 | 223 | [6 empty] | 0 |  | 0
2021-08-28 | 235 | [6 empty] | 0 |  | 0
2021-08-29 | 236 | [6 empty] | 0 |  | 0
2021-08-30 | 241 | [6 empty] | 0 |  | 0
2021-08-31 | 239 | [6 empty] | 0 |  | 0
MINIMUM | 69 | 4 | 1 | 1 | 7 | 3.7 | 1.3 | 0 | 0 | 0
AVERAGE | 463.9368 | 9.9167 | 141.7 | 1 | 25.3833 | 5.9 | 1.975 | 0 | #DIV/0! | 2.6849
MAXIMUM | 2400 | 23 | 727 | 1 | 59 | 9.3 | 4.2 | 0 | 0 | 205
TOTAL | 168873 | [6 empty] | 0 |  | 980
SAMPLE COUNT |  | 12
Non-compliant Results | 24 | 1 |  | 0 | 2 |  |  |  | 0

## 21-22
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 21/22
EPA Licence Number: 351 - Box Ridge Road Coraki
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Sample Collected By | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2021-09-01 | 238 | [6 empty] | 0 |  | 0
2021-09-02 | 246 | [6 empty] | 0 |  | 0
2021-09-03 | 243 | [6 empty] | 0 |  | 0
2021-09-04 | 257 | [6 empty] | 0 |  | 0
2021-09-05 | 254 | [6 empty] | 0 |  | 0
2021-09-06 | 221 | [6 empty] | 0 |  | 0
2021-09-07 | 251 | [6 empty] | 0 |  | 0
2021-09-08 | 236 | 17 | 125 | 0.01 | 44 | 9.1 | 4.3 | 0 |  | 0 | 9:00 | Craig Smith | 22.09.2021 | 11.10.2021
2021-09-09 | 231 | [6 empty] | 0 |  | 0
2021-09-10 | 238 | [6 empty] | 0 |  | 0
2021-09-11 | 253 | [6 empty] | 0 |  | 0
2021-09-12 | 246 | [6 empty] | 0 |  | 0
2021-09-13 | 240 | [6 empty] | 0 |  | 0
2021-09-14 | 242 | [6 empty] | 0 |  | 0
2021-09-15 | 245 | [6 empty] | 0 |  | 0
2021-09-16 | 243 | [6 empty] | 0 |  | 0
2021-09-17 | 243 | [6 empty] | 0 |  | 0
2021-09-18 | 249 | [6 empty] | 0 |  | 0
2021-09-19 | 239 | [6 empty] | 0 |  | 0
2021-09-20 | 258 | [6 empty] | 0 |  | 0
2021-09-21 | 236 | [6 empty] | 0 |  | 10
2021-09-22 | 233 | [6 empty] | 0 |  | 0
2021-09-23 | 226 | [6 empty] | 0 |  | 0
2021-09-24 | 228 | [6 empty] | 0 |  | 0
2021-09-25 | 231 | [6 empty] | 0 |  | 0
2021-09-26 | 233 | [6 empty] | 0 |  | 0
2021-09-27 | 245 | [6 empty] | 0 |  | 10
2021-09-28 | 225 | [6 empty] | 0 |  | 0
2021-09-29 | 234 | [6 empty] | 0 |  | 0
2021-09-30 | 282 | [6 empty] | 0 |  | 10
2021-10-01 | 289 | [6 empty] | 0 |  | 5
2021-10-02 | 255 | [6 empty] | 0 |  | 6
2021-10-03 | 251 | [6 empty] | 0 |  | 0
2021-10-04 | 241 | [6 empty] | 0 |  | 0
2021-10-05 | 225 | [6 empty] | 0 |  | 0
2021-10-06 | 235 | [6 empty] | 0 |  | 0
2021-10-07 | 226 | [6 empty] | 0 |  | 0
2021-10-08 | 234 | [6 empty] | 0 |  | 0
2021-10-09 | 243 | [6 empty] | 0 |  | 0
2021-10-10 | 241 | [6 empty] | 0 |  | 0
2021-10-11 | 261 | [6 empty] | 0 |  | 0
2021-10-12 | 753 | [6 empty] | 0 |  | 16
2021-10-13 | 492 | 4 | 260 | 0.01 | 52 | 5.7 | 1.3 | 0 |  | 40 | 8:00 | Craig Smith | 21.10.2021 | 22.10.2021
2021-10-14 | 340 | [6 empty] | 0 |  | 0
2021-10-15 | 281 | [6 empty] | 0 |  | 0
2021-10-16 | 276 | [6 empty] | 0 |  | 0
2021-10-17 | 265 | [6 empty] | 0 |  | 0
2021-10-18 | 587 | [6 empty] | 0 |  | 0
2021-10-19 | 431 | [6 empty] | 0 |  | 28
2021-10-20 | 322 | [6 empty] | 0 |  | 5
2021-10-21 | 403 | [6 empty] | 0 |  | 25
2021-10-22 | 390 | [6 empty] | 0 |  | 0
2021-10-23 | 359 | [6 empty] | 0 |  | 0
2021-10-24 | 320 | [6 empty] | 0 |  | 0
2021-10-25 | 271 | [6 empty] | 0 |  | 0
2021-10-26 | 256 | [6 empty] | 0 |  | 0
2021-10-27 | 104 | [6 empty] | 0 |  | 0
2021-10-28 | 233 | [6 empty] | 0 |  | 0
2021-10-29 | 222 | [6 empty] | 0 |  | 0
2021-10-30 | 239 | [6 empty] | 0 |  | 0
2021-10-31 | 219 | [6 empty] | 0 |  | 0
2021-11-01 | 236 | [6 empty] | 0 |  | 0
2021-11-02 | 222 | [6 empty] | 0 |  | 0
2021-11-03 | 232 | [6 empty] | 0 |  | 0
2021-11-04 | 222 | [6 empty] | 0 |  | 0
2021-11-05 | 233 | [6 empty] | 0 |  | 0
2021-11-06 | 237 | [6 empty] | 0 |  | 0
2021-11-07 | 239 | [6 empty] | 0 |  | 0
2021-11-08 | 282 | [6 empty] | 0 |  | 0
2021-11-09 | 246 | [6 empty] | 0 |  | 0
2021-11-10 | 279 | 6 | 0.01 | 0.01 | 23 | 3.8 | 0.81 | 0 |  | 0 | 9:30 | Craig Smith | 2021-11-16 | 2021-11-16
2021-11-11 | 766 | [6 empty] | 0 |  | 0
2021-11-12 | 387 | [6 empty] | 0 |  | 0
2021-11-13 | 299 | [6 empty] | 0 |  | 0
2021-11-14 | 270 | [6 empty] | 0 |  | 0
2021-11-15 | 259 | [6 empty] | 0 |  | 0
2021-11-16 | 217 | [6 empty] | 0 |  | 0
2021-11-17 | 263 | [6 empty] | 0 |  | 0
2021-11-18 | 240 | [6 empty] | 0 |  | 0
2021-11-19 | 234 | [6 empty] | 0 |  | 0
2021-11-20 | 238 | [6 empty] | 0 |  | 0
2021-11-21 | 325 | [6 empty] | 0 |  | 0
2021-11-22 | 271 | [6 empty] | 0 |  | 23
2021-11-23 | 327 | [6 empty] | 0 |  | 7
2021-11-24 | 336 | [6 empty] | 0 |  | 15
2021-11-25 | 420 | [6 empty] | 0 |  | 1
2021-11-26 | 571 | [6 empty] | 0 |  | 0
2021-11-27 | 522 | [6 empty] | 0 |  | 0
2021-11-28 | 343 | [6 empty] | 0 |  | 0
2021-11-29 | 295 | [6 empty] | 0 |  | 7
2021-11-30 | 1030 | [6 empty] | 0 |  | 95
2021-12-01 | 1928 | [6 empty] | 0 |  | 10
2021-12-02 | 1003 | [6 empty] | 0 |  | 0
2021-12-03 | 608 | [6 empty] | 0 |  | 0
2021-12-04 | 810 | [6 empty] | 0 |  | 0
2021-12-05 | 887 | [6 empty] | 0 |  | 0
2021-12-06 | 842 | [6 empty] | 0 |  | 0
2021-12-07 | 607 | [6 empty] | 0 |  | 0
2021-12-08 | 677 | 12 | 105 | 0.01 | 50 | 7.4 | 1.7 | 0 |  | 0 | 9:00 | Craig Smith | 2021-12-15 | 2021-12-16
2021-12-09 | 1308 | [6 empty] | 0 |  | 9
2021-12-10 | 852 | [6 empty] | 0 |  | 0
2021-12-11 | 550 | [6 empty] | 0 |  | 0
2021-12-12 | 470 | [6 empty] | 0 |  | 0
2021-12-13 | 414 | [6 empty] | 0 |  | 0
2021-12-14 | 379 | [6 empty] | 0 |  | 0
2021-12-15 | 357 | [6 empty] | 0 |  | 0
2021-12-16 | 351 | [6 empty] | 0 |  | 0
2021-12-17 | 334 | [6 empty] | 0 |  | 2
2021-12-18 | 339 | [6 empty] | 0 |  | 3
2021-12-19 | 324 | [6 empty] | 0 |  | 0
2021-12-20 | 304 | [6 empty] | 0 |  | 0
2021-12-21 | 282 | [6 empty] | 0 |  | 0
2021-12-22 | 305 | [6 empty] | 0 |  | 0
2021-12-23 | 313 | [6 empty] | 0 |  | 0
2021-12-24 | 294 | [6 empty] | 0 |  | 4
2021-12-25 | 281 | [6 empty] | 0 |  | 0
2021-12-26 | 215 | [6 empty] | 0 |  | 0
2021-12-27 | 371 | [6 empty] | 0 |  | 50
2021-12-28 | 946 | [6 empty] | 0 |  | 8
2021-12-29 | 485 | [6 empty] | 0 |  | 0
2021-12-30 | 403 | [6 empty] | 0 |  | 0
2021-12-31 | 389 | [6 empty] | 0 |  | 0
2022-01-01 | 456 | [6 empty] | 0 |  | 0
2022-01-02 | 369 | [6 empty] | 0 |  | 0
2022-01-03 | 384 | [6 empty] | 0 |  | 20
2022-01-04 | 434 | [6 empty] | 0 |  | 15
2022-01-05 | 603 | 15 | 2 | 1 | 45 | 4 | 1.6 | 0 |  | 0 | 9.00 AM | Craig Smith | 12.01.2022 | 13.01.2022
2022-01-06 | 564 | [6 empty] | 0 |  | 2
2022-01-07 | 426 | [6 empty] | 0 |  | 3
2022-01-08 | 379 | [6 empty] | 0 |  | 0
2022-01-09 | 394 | [6 empty] | 0 |  | 0
2022-01-10 | 383 | [6 empty] | 0 |  | 6
2022-01-11 | 327 | [6 empty] | 0 |  | 0
2022-01-12 | 306 | [6 empty] | 0 |  | 0
2022-01-13 | 290 | [6 empty] | 0 |  | 0
2022-01-14 | 301 | [6 empty] | 0 |  | 0
2022-01-15 | 294 | [6 empty] | 0 |  | 0
2022-01-16 | 361 | [6 empty] | 0 |  | 0
2022-01-17 | 293 | [6 empty] | 0 |  | 15
2022-01-18 | 287 | [6 empty] | 0 |  | 0
2022-01-19 | 318 | [6 empty] | 0 |  | 18
2022-01-20 | 1256 | [6 empty] | 0 |  | 56
2022-01-21 | 1229 | [6 empty] | 0 |  | 8
2022-01-22 | 847 | [6 empty] | 0 |  | 0
2022-01-23 | 524 | [6 empty] | 0 |  | 0
2022-01-24 | 486 | [6 empty] | 0 |  | 6
2022-01-25 | 439 | [6 empty] | 0 |  | 0
2022-01-26 | 498 | [6 empty] | 0 |  | 9
2022-01-27 | 418 | [6 empty] | 0 |  | 0
2022-01-28 | 594 | [6 empty] | 0 |  | 0
2022-01-29 | 528 | [6 empty] | 0 |  | 0
2022-01-30 | 431 | [6 empty] | 0 |  | 0
2022-01-31 | 389 | [6 empty] | 0 |  | 0
2022-02-01 | 384 | [6 empty] | 0 |  | 8
2022-02-02 | 671 | 6 | 19 | 2 | 17 | 2.8 | 2.2 | 0 |  | 46 |  | Shane White | 11.02.2022 | 14.02.2022
2022-02-03 | 1913 | [6 empty] | 0 |  | 50
2022-02-04 | 1610 | [6 empty] | 0 |  | 7
2022-02-05 | 889 | [6 empty] | 0 |  | 0
2022-02-06 | 727 | [6 empty] | 0 |  | 9
2022-02-07 | 620 | [6 empty] | 0 |  | 0
2022-02-08 | 550 | [6 empty] | 0 |  | 5
2022-02-09 | 488 | [6 empty] | 0 |  | 0
2022-02-10 | 444 | [6 empty] | 0 |  | 0
2022-02-11 | 429 | [6 empty] | 0 |  | 0
2022-02-12 | 414 | [6 empty] | 0 |  | 2
2022-02-13 | 387 | [6 empty] | 0
2022-02-14 | 377 | [6 empty] | 0
2022-02-15 | 382 | [6 empty] | 0 |  | 9
2022-02-16 | 369 | [6 empty] | 0
2022-02-17 | 365 | [6 empty] | 0
2022-02-18 | 375 | [6 empty] | 0
2022-02-19 | 355 | [6 empty] | 0 |  | 12
2022-02-20 | 338 | [6 empty] | 0
2022-02-21 | 330 | [6 empty] | 0 |  | 4
2022-02-22 | 329 | [6 empty] | 0 |  | 2
2022-02-23 | 1374 | [6 empty] | 0
2022-02-24 | 2171 | [6 empty] | 0 |  | 10
2022-02-25 | 1812 | [6 empty] | 0
2022-02-26 | 1873 | [6 empty] | 0
2022-02-27 | 2034 | [6 empty] | 0
2022-02-28 | 1933 | [6 empty] | 0
2022-03-01 | 0 | [6 empty] | 0
2022-03-02 | 0 | [6 empty] | 0
2022-03-03 | 0 | [6 empty] | 0
2022-03-04 | 0 | [6 empty] | 0
2022-03-05 | 0 | [6 empty] | 0
2022-03-06 | 0 | [6 empty] | 0 |  | 70
2022-03-07 | 0 | [6 empty] | 0 |  | 40
2022-03-08 | 3446 | [6 empty] | 0
2022-03-09 | 1990 | 5 | 200 | <2 | 41 | 1.4 | 0.94 | 0 |  | 10 | 9.00AM | Craig Smith | 2022-03-09 | 2022-05-20
2022-03-10 | 1942 | [6 empty] | 0
2022-03-11 | 1854 | [6 empty] | 0 |  | 9
2022-03-12 | 1086 | [6 empty] | 0 |  | 0
2022-03-13 | 1025 | [6 empty] | 0
2022-03-14 | 898 | [6 empty] | 0 |  | 10
2022-03-15 | 725 | [6 empty] | 0
2022-03-16 | 653 | [6 empty] | 0
2022-03-17 | 618 | [6 empty] | 0 |  | 7
2022-03-18 | 593 | [6 empty] | 0 |  | 3
2022-03-19 | 556 | [6 empty] | 0
2022-03-20 | 504 | [6 empty] | 0
2022-03-21 | 474 | [6 empty] | 0
2022-03-22 | 446 | [6 empty] | 0
2022-03-23 | 421 | [6 empty] | 0
2022-03-24 | 579 | [6 empty] | 0 |  | 26
2022-03-25 | 709 | [6 empty] | 0 |  | 15
2022-03-26 | 1396 | [6 empty] | 0
2022-03-27 | 1997 | [6 empty] | 0 |  | 85
2022-03-28 | 1970 | [6 empty] | 0 |  | 100
2022-03-29 | 2076 | [6 empty] | 0 |  | 200
2022-03-30 | 1444 | [6 empty] | 0
2022-03-31 | 1951 | [6 empty] | 0
2022-04-01 | 2059 | [6 empty] | 0
2022-04-02 | 2050 | [6 empty] | 0 |  | 20
2022-04-03 | 1940 | [6 empty] | 0 |  | 15
2022-04-04 | 2004 | [6 empty] | 0
2022-04-05 | 2008 | [6 empty] | 0
2022-04-06 | 2027 | 6 | 920 | <2 | 16 | 2.3 | 0.85 | 0 |  | 15 | 08.30AM | Craig Smith | 2022-05-25 | 2022-06-08
2022-04-07 | 1430 | [6 empty] | 0 |  | 7
2022-04-08 | 1053 | [6 empty] | 0 |  | 22
2022-04-09 | 1360 | [6 empty] | 0
2022-04-10 | 949 | [6 empty] | 0
2022-04-11 | 756 | [6 empty] | 0 |  | 10
2022-04-12 | 626 | [6 empty] | 0
2022-04-13 | 698 | [6 empty] | 0 |  | 5
2022-04-14 | 788 | [6 empty] | 0 |  | 12
2022-04-15 | 696 | [6 empty] | 0 |  | 4
2022-04-16 | 612 | [6 empty] | 0
2022-04-17 | 617 | [6 empty] | 0
2022-04-18 | 546 | [6 empty] | 0
2022-04-19 | 501 | [6 empty] | 0
2022-04-20 | 472 | [6 empty] | 0
2022-04-21 | 435 | [6 empty] | 0
2022-04-22 | 657 | [6 empty] | 0
2022-04-23 | 925 | [6 empty] | 0 |  | 30
2022-04-24 | 879 | [6 empty] | 0
2022-04-25 | 680 | [6 empty] | 0 |  | 10
2022-04-26 | 565 | [6 empty] | 0 |  | 3
2022-04-27 | 508 | 12 | 41 | <2 | 36 | 5.3 | 0.73 | 0 |  |  | 07.20 AM | Craig Smith | 2022-06-08 | 2022-06-08
2022-04-28 | 487 | [6 empty] | 0
2022-04-29 | 484 | [6 empty] | 0 |  | 8
2022-04-30 | 459 | [6 empty] | 0 |  | 3
2022-05-01 | 729 | [6 empty] | 0 |  | 20
2022-05-02 | 750 | [6 empty] | 0
2022-05-03 | 667 | [6 empty] | 0 |  | 7
2022-05-04 | 648 | [6 empty] | 0
2022-05-05 | 548 | [6 empty] | 0
2022-05-06 | 590 | [6 empty] | 0
2022-05-07 | 699 | [6 empty] | 0
2022-05-08 | 1049 | [6 empty] | 0
2022-05-09 | 643 | [6 empty] | 0
2022-05-10 | 636 | [6 empty] | 0
2022-05-11 | 630 | [6 empty] | 0
2022-05-12 | 701 | [6 empty] | 0 |  | 6
2022-05-13 | 617 | [6 empty] | 0 |  | 2
2022-05-14 | 1000 | [6 empty] | 0 |  | 13
2022-05-15 | 1557 | [6 empty] | 0 |  | 28
2022-05-16 | 886 | [6 empty] | 0
2022-05-17 | 690 | [6 empty] | 0
2022-05-18 | 591 | [6 empty] | 0
2022-05-19 | 526 | [6 empty] | 0
2022-05-20 | 508 | [6 empty] | 0 |  | 4
2022-05-21 | 1808 | [6 empty] | 0 |  | 32
2022-05-22 | 2018 | [6 empty] | 0
2022-05-23 | 2020 | [6 empty] | 0 |  | 80
2022-05-24 | 1918 | [6 empty] | 0 |  | 20
2022-05-25 | 1828 | 5 | 2400 | <2 | 18 | 6.2 | 0.73 | 0 |  | 23 | 07:55AM | Craig Smith | 2022-06-21 | 2022-06-23
2022-05-26 | 1304 | [6 empty] | 0 |  | 10
2022-05-27 | 1044 | [6 empty] | 0 |  | 6
2022-05-28 | 897 | [6 empty] | 0
2022-05-29 | 865 | [6 empty] | 0 |  | 8
2022-05-30 | 691 | [6 empty] | 0
2022-05-31 | 605 | [6 empty] | 0
2022-06-01 | 546 | [6 empty] | 0
2022-06-02 | 498 | [6 empty] | 0
2022-06-03 | 680 | [6 empty] | 0 |  | 15
2022-06-04 | 679 | [6 empty] | 0
2022-06-05 | 578 | [6 empty] | 0
2022-06-06 | 505 | [6 empty] | 0
2022-06-07 | 453 | [6 empty] | 0
2022-06-08 | 436 | [6 empty] | 0
2022-06-09 | 415 | [6 empty] | 0
2022-06-10 | 398 | [6 empty] | 0
2022-06-11 | 401 | [6 empty] | 0
2022-06-12 | 403 | [6 empty] | 0
2022-06-13 | 398 | [6 empty] | 0
2022-06-14 | 381 | [6 empty] | 0
2022-06-15 | 362 | [6 empty] | 0
2022-06-16 | 352 | [6 empty] | 0
2022-06-17 | 346 | [6 empty] | 0
2022-06-18 | 343 | [6 empty] | 0
2022-06-19 | 342 | [6 empty] | 0
2022-06-20 | 322 | [6 empty] | 0
2022-06-21 | 334 | [6 empty] | 0
2022-06-22 | 331 | 11 |  | <2 | 27 | 6.5 | 0.81 | 0 |  |  | 08:00AM | Craig Smith | 2022-07-01 | 2022-07-12
2022-06-23 | 316 | [6 empty] | 0
2022-06-24 | 318 | [6 empty] | 0
2022-06-25 | 309 | [6 empty] | 0
2022-06-26 | 309 | [6 empty] | 0
2022-06-27 | 303 | [6 empty] | 0
2022-06-28 | 300 | [6 empty] | 0
2022-06-29 | 305 | [6 empty] | 0
2022-06-30 | 301 | [6 empty] | 0
2022-07-01 | 325 | [6 empty] | 0
2022-07-02 | 545 | [6 empty] | 0 |  | 23
2022-07-03 | 458 | [6 empty] | 0 |  | 5
2022-07-04 | 375 | [6 empty] | 0 |  | 15
2022-07-05 | 938 | [6 empty] | 0 |  | 30
2022-07-06 | 1388 | [6 empty] | 0 |  | 10
2022-07-07 | 734 | [6 empty] | 0
2022-07-08 | 566 | [6 empty] | 0 |  | 4
2022-07-09 | 477 | [6 empty] | 0
2022-07-10 | 434 | [6 empty] | 0
2022-07-11 | 394 | [6 empty] | 0
2022-07-12 | 380 | [6 empty] | 0
2022-07-13 | 378 | [6 empty] | 0
2022-07-14 | 351 | [6 empty] | 0
2022-07-15 | 341 | [6 empty] | 0
2022-07-16 | 332 | [6 empty] | 0
2022-07-17 | 330 | [6 empty] | 0
2022-07-18 | 314 | [6 empty] | 0
2022-07-19 | 314 | 5 |  | 2 | 25 | 9.3 | 0.94 | 0 |  |  | 09:00AM | Craig Smith | 2022-08-01 | 2022-08-01
2022-07-20 | 386 | [6 empty] | 0
2022-07-21 | 521 | [6 empty] | 0
2022-07-22 | 1314 | [6 empty] | 0
2022-07-23 | 949 | [6 empty] | 0
2022-07-24 | 646 | [6 empty] | 0
2022-07-25 | 521 | [6 empty] | 0
2022-07-26 | 474 | [6 empty] | 0
2022-07-27 | 429 | [6 empty] | 0
2022-07-28 | 388 | [6 empty] | 0
2022-07-29 | 372 | [6 empty] | 0
2022-07-30 | 362 | [6 empty] | 0
2022-07-31 | 358 | [6 empty] | 0
2022-08-01 | 339 | [6 empty] | 0
2022-08-02 | 361 | [6 empty] | 0
2022-08-03 | 339 | [6 empty] | 0
2022-08-04 | 336 | [6 empty] | 0
2022-08-05 | 330 | [6 empty] | 0
2022-08-06 | 333 | [6 empty] | 0
2022-08-07 | 333 | [6 empty] | 0
2022-08-08 | 313 | [6 empty] | 0
2022-08-09 | 308 | [6 empty] | 0
2022-08-10 | 301 | [6 empty] | 0
2022-08-11 | 299 | [6 empty] | 0
2022-08-12 | 282 | [6 empty] | 0
2022-08-13 | 304 | [6 empty] | 0
2022-08-14 | 320 | [6 empty] | 0
2022-08-15 | 296 | [6 empty] | 0
2022-08-16 | 302 | 8 |  | <2 | 29 | 9.6 | 1.1 | 0 |  |  | 09:00AM | Craig Smith | 2022-08-26 | 2022-08-26
2022-08-17 | 295 | [6 empty] | 0
2022-08-18 | 331 | [6 empty] | 0
2022-08-19 | 295 | [6 empty] | 0
2022-08-20 | 289 | [6 empty] | 0
2022-08-21 | 284 | [6 empty] | 0
2022-08-22 | 288 | [6 empty] | 0
2022-08-23 | 275 | [6 empty] | 0
2022-08-24 | 278 | [6 empty] | 0
2022-08-25 | 278 | [6 empty] | 0
2022-08-26 | 268 | [6 empty] | 0
2022-08-27 | 267 | [6 empty] | 0
2022-08-28 | 269 | [6 empty] | 0
2022-08-29 | 290 | [6 empty] | 0
2022-08-30 | 268 | [6 empty] | 0
2022-08-31 | 283 | [6 empty] | 0
MINIMUM | 0 | 4 | 0.01 | 0.01 | 16 | 1.4 | 0.73 | 0 | 0 | 0
AVERAGE | 572.1342 | 8.6154 | 407.201 | 0.72 | 32.5385 | 5.6462 | 1.3854 | 0 | #DIV/0! | 4.1227
MAXIMUM | 3446 | 17 | 2400 | 2 | 52 | 9.6 | 4.3 | 0 | 0 | 95
TOTAL | 208829 | [6 empty] | 0 |  | 771.1227
SAMPLE COUNT |  | 13
Non-compliant Results | 37 | 0 |  | 0 | 6 |  |  |  | 0

## 22-23
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 22/23
EPA Licence Number: 351 - Box Ridge Road Coraki
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Sample Collected By | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2022-09-01 | 262 | [6 empty] | 0 |  | 0
2022-09-02 | 274 | [6 empty] | 0 |  | 0
2022-09-03 | 292 | [6 empty] | 0 |  | 0
2022-09-04 | 714 | [6 empty] | 0 |  | 0
2022-09-05 | 466 | [6 empty] | 0 |  | 26
2022-09-06 | 393 | [6 empty] | 0 |  | 0
2022-09-07 | 365 | [6 empty] | 0 |  | 0
2022-09-08 | 343 | [6 empty] | 0 |  | 0
2022-09-09 | 406 | [6 empty] | 0 |  | 10
2022-09-10 | 388 | [6 empty] | 0 |  | 3
2022-09-11 | 354 | [6 empty] | 0 |  | 0
2022-09-12 | 314 | [6 empty] | 0 |  | 0
2022-09-13 | 309 | [6 empty] | 0 |  | 0
2022-09-14 | 303 | [6 empty] | 0 |  | 0
2022-09-15 | 297 | [6 empty] | 0 |  | 0
2022-09-16 | 322 | [6 empty] | 0 |  | 7
2022-09-17 | 307 | [6 empty] | 0 |  | 0
2022-09-18 | 302 | [6 empty] | 0 |  | 0
2022-09-19 | 363 | [6 empty] | 0 |  | 0
2022-09-20 | 326 | [6 empty] | 0 |  | 0
2022-09-21 | 202 | [6 empty] | 0 |  | 0
2022-09-22 | 1209 | [6 empty] | 0 |  | 17
2022-09-23 | 1410 | [6 empty] | 0 |  | 51
2022-09-24 | 732 | [6 empty] | 0 |  | 13
2022-09-25 | 520 | [6 empty] | 0 |  | 0
2022-09-26 | 423 | [6 empty] | 0 |  | 0
2022-09-27 | 389 | 5 |  | <2 | 40 | 8.7 | 1.1 | 0 |  | 3 | 10:00 | Stephen Scott | 2022-09-27 | 2022-10-04
2022-09-28 | 367 | [6 empty] | 0 |  | 0
2022-09-29 | 353 | [6 empty] | 0 |  | 0
2022-09-30 | 339 | [6 empty] | 0 |  | 0
2022-10-01 | 456 | [6 empty] | 0 |  | 0
2022-10-02 | 796 | [6 empty] | 0 |  | 0
2022-10-03 | 532 | [6 empty] | 0 |  | 30
2022-10-04 | 425 | [6 empty] | 0 |  | 0
2022-10-05 | 367 | [6 empty] | 0 |  | 0
2022-10-06 | 351 | [6 empty] | 0 |  | 4
2022-10-07 | 359 | [6 empty] | 0 |  | 0
2022-10-08 | 356 | [6 empty] | 0 |  | 0
2022-10-09 | 347 | [6 empty] | 0 |  | 0
2022-10-10 | 327 | [6 empty] | 0 |  | 6
2022-10-11 | 335 | [6 empty] | 0 |  | 6
2022-10-12 | 327 | 6 | 12 | <2 | 33 | 7.1 | 0.87 | 0 |  | 4 | 10:00 | Stephen Scott | 2022-10-26 | 2022-11-21
2022-10-13 | 313 | [6 empty] | 0 |  | 2
2022-10-14 | 312 | [6 empty] | 0 |  | 0
2022-10-15 | 310 | [6 empty] | 0 |  | 0
2022-10-16 | 302 | [6 empty] | 0 |  | 0
2022-10-17 | 465 | [6 empty] | 0 |  | 0
2022-10-18 | 433 | [6 empty] | 0 |  | 15
2022-10-19 | 359 | [6 empty] | 0 |  | 0
2022-10-20 | 412 | [6 empty] | 0 |  | 8
2022-10-21 | 380 | [6 empty] | 0 |  | 3
2022-10-22 | 400 | [6 empty] | 0 |  | 6
2022-10-23 | 1612 | [6 empty] | 0 |  | 0
2022-10-24 | 2003 | [6 empty] | 0 |  | 140
2022-10-25 | 1462 | [6 empty] | 0 |  | 16
2022-10-26 | 779 | [6 empty] | 0 |  | 0
2022-10-27 | 589 | [6 empty] | 0 |  | 0
2022-10-28 | 501 | [6 empty] | 0 |  | 0
2022-10-29 | 451 | [6 empty] | 0 |  | 0
2022-10-30 | 414 | [6 empty] | 0 |  | 0
2022-10-31 | 377 | [6 empty] | 0 |  | 0
2022-11-01 | 393 | [6 empty] | 0 |  | 5
2022-11-02 | 374 | [6 empty] | 0 |  | 3
2022-11-03 | 350 | [6 empty] | 0 |  | 0
2022-11-04 | 333 | [6 empty] | 0 |  | 0
2022-11-05 | 342 | [6 empty] | 0 |  | 0
2022-11-06 | 351 | [6 empty] | 0 |  | 0
2022-11-07 | 334 | 5 | 1 | <2 | 8 | 3.6 | 0.86 | 0 |  | 4 | 14:00 | Stephen Scott | 2022-11-18 | 2022-11-21
2022-11-08 | 368 | [6 empty] | 0 |  | 0
2022-11-09 | 342 | [6 empty] | 0 |  | 0
2022-11-10 | 325 | [6 empty] | 0 |  | 1
2022-11-11 | 322 | [6 empty] | 0 |  | 0
2022-11-12 | 327 | [6 empty] | 0 |  | 0
2022-11-13 | 316 | [6 empty] | 0 |  | 0
2022-11-14 | 302 | [6 empty] | 0 |  | 0
2022-11-15 | 288 | [6 empty] | 0 |  | 0
2022-11-16 | 284 | [6 empty] | 0 |  | 0
2022-11-17 | 276 | [6 empty] | 0 |  | 0
2022-11-18 | 273 | [6 empty] | 0 |  | 0
2022-11-19 | 280 | [6 empty] | 0 |  | 0
2022-11-20 | 284 | [6 empty] | 0 |  | 0
2022-11-21 | 257 | [6 empty] | 385 |  | 0
2022-11-22 | 261 | [6 empty] | 338 |  | 0
2022-11-23 | 256 | [6 empty] | 0 |  | 0
2022-11-24 | 263 | [6 empty] | 0 |  | 0
2022-11-25 | 259 | [6 empty] | 0 |  | 0
2022-11-26 | 257 | [6 empty] | 0 |  | 0
2022-11-27 | 261 | [6 empty] | 0 |  | 0
2022-11-28 | 237 | [6 empty] | 0 |  | 0
2022-11-29 | 198 | [6 empty] | 0 |  | 0
2022-11-30 | 175 | [6 empty] | 109 |  | 0
2022-12-01 | 315 | [6 empty] | 0 |  | 12
2022-12-02 | 248 | [6 empty] | 0 |  | 31
2022-12-03 | 246 | [6 empty] | 0 |  | 0
2022-12-04 | 304 | [6 empty] | 0 |  | 0
2022-12-05 | 285 | [6 empty] | 0 |  | 5
2022-12-06 | 272 | 5 | 21 | <2 | 11 | 3.3 | 0.65 | 244 |  | 0 | 7:30 | Stephen Scott | 2022-12-15 | 2023-01-04
2022-12-07 | 255 | [6 empty] | 0 |  | 0
2022-12-08 | 264 | [6 empty] | 0 |  | 0
2022-12-09 | 244 | [6 empty] | 0 |  | 0
2022-12-10 | 245 | [6 empty] | 0 |  | 0
2022-12-11 | 256 | [6 empty] | 0 |  | 0
2022-12-12 | 247 | [6 empty] | 214 |  | 0
2022-12-13 | 237 | [6 empty] | 0 |  | 2
2022-12-14 | 240 | [6 empty] | 0 |  | 0
2022-12-15 | 234 | [6 empty] | 349 |  | 0
2022-12-16 | 238 | [6 empty] | 0 |  | 0
2022-12-17 | 235 | [6 empty] | 0 |  | 0
2022-12-18 | 240 | [6 empty] | 0 |  | 0
2022-12-19 | 229 | [6 empty] | 0 |  | 0
2022-12-20 | 229 | [6 empty] | 0 |  | 0
2022-12-21 | 237 | [6 empty] | 420 |  | 0
2022-12-22 | 230 | [6 empty] | 0 |  | 0
2022-12-23 | 227 | [6 empty] | 0 |  | 0
2022-12-24 | 232 | [6 empty] | 0 |  | 2
2022-12-25 | 208 | [6 empty] | 0 |  | 2
2022-12-26 | 223 | [6 empty] | 0 |  | 0
2022-12-27 | 221 | [6 empty] | 0 |  | 0
2022-12-28 | 223 | [6 empty] | 0 |  | 3
2022-12-29 | 221 | [6 empty] | 0 |  | 0
2022-12-30 | 228 | [6 empty] | 0 |  | 3
2022-12-31 | 232 | [6 empty] | 0 |  | 2
2023-01-01 | 207 | [6 empty] | 0 |  | 0
2023-01-02 | 225 | [6 empty] | 0 |  | 0
2023-01-03 | 221 | 14 | 1 | <2 | 74 | 9 | 1.1 | 511 |  | 0 | 10:30 | Stephen Scott | 2023-01-16 | 2023-03-24
2023-01-04 | 268 | [6 empty] | 395 |  | 0
2023-01-05 | 485 | [6 empty] | 0 |  | 32
2023-01-06 | 279 | [6 empty] | 0 |  | 19
2023-01-07 | 239 | [6 empty] | 0 |  | 0
2023-01-08 | 240 | [6 empty] | 0 |  | 0
2023-01-09 | 231 | [6 empty] | 0 |  | 0
2023-01-10 | 216 | [6 empty] | 0 |  | 0
2023-01-11 | 224 | [6 empty] | 0 |  | 0
2023-01-12 | 219 | [6 empty] | 395 |  | 0
2023-01-13 | 209 | [6 empty] | 0 |  | 0
2023-01-14 | 214 | [6 empty] | 0 |  | 0
2023-01-15 | 221 | [6 empty] | 0 |  | 0
2023-01-16 | 212 | [6 empty] | 0 |  | 0
2023-01-17 | 204 | [6 empty] | 0 |  | 0
2023-01-18 | 202 | [6 empty] | 0 |  | 0
2023-01-19 | 215 | [6 empty] | 318 |  | 0
2023-01-20 | 406 | [6 empty] | 0 |  | 37
2023-01-21 | 243 | [6 empty] | 0 |  | 0
2023-01-22 | 221 | [6 empty] | 0 |  | 0
2023-01-23 | 233 | [6 empty] | 0 |  | 0
2023-01-24 | 234 | [6 empty] | 0 |  | 7
2023-01-25 | 243 | [6 empty] | 0 |  | 6
2023-01-26 | 223 | [6 empty] | 0 |  | 8
2023-01-27 | 206 | [6 empty] | 0 |  | 0
2023-01-28 | 214 | [6 empty] | 0 |  | 0
2023-01-29 | 226 | [6 empty] | 0 |  | 0
2023-01-30 | 216 | [6 empty] | 0 |  | 0
2023-01-31 | 461 | [6 empty] | 0 |  | 20
2023-02-01 | 321 | [6 empty] | 0 |  | 0
2023-02-02 | 232 | [6 empty] | 0 |  | 0
2023-02-03 | 220 | [6 empty] | 0 |  | 0
2023-02-04 | 217 | [6 empty] | 0 |  | 0
2023-02-05 | 230 | [6 empty] | 0 |  | 0
2023-02-06 | 218 | [6 empty] | 0 |  | 0
2023-02-07 | 215 | [6 empty] | 0 |  | 0
2023-02-08 | 211 | [6 empty] | 0 |  | 0
2023-02-09 | 202 | [6 empty] | 0 |  | 0
2023-02-10 | 208 | [6 empty] | 0 |  | 0
2023-02-11 | 214 | [6 empty] | 0 |  | 0
2023-02-12 | 229 | [6 empty] | 0 |  | 0
2023-02-13 | 210 | [6 empty] | 0 |  | 0
2023-02-14 | 219 | 20 | 6 | <2 | 74 | 9 | 1.1 | 0 |  | 0 | 9:00 | Stephen Scott | 2023-02-22 | 2023-03-24
2023-02-15 | 219 | [6 empty] | 0 |  | 4
2023-02-16 | 204 | [6 empty] | 436 |  | 0
2023-02-17 | 204 | [6 empty] | 0 |  | 0
2023-02-18 | 208 | [6 empty] | 0 |  | 0
2023-02-19 | 229 | [6 empty] | 0 |  | 0
2023-02-20 | 206 | [6 empty] | 0 |  | 0
2023-02-21 | 203 | [6 empty] | 146 |  | 0
2023-02-22 | 212 | [6 empty] | 142 |  | 4
2023-02-23 | 228 | [6 empty] | 0 |  | 0
2023-02-24 | 269 | [6 empty] | 0 |  | 19
2023-02-25 | 223 | [6 empty] | 0 |  | 4
2023-02-26 | 224 | [6 empty] | 0 |  | 0
2023-02-27 | 203 | [6 empty] | 0 |  | 0
2023-02-28 | 201 | [6 empty] | 0 |  | 0
2023-03-01 | 216 | [6 empty] | 0 |  | 0
2023-03-02 | 299 | [6 empty] | 0 |  | 12
2023-03-03 | 277 | [6 empty] | 0 |  | 15
2023-03-04 | 218 | [6 empty] | 0 |  | 3
2023-03-05 | 222 | [6 empty] | 0 |  | 0
2023-03-06 | 213 | [6 empty] | 0 |  | 0
2023-03-07 | 203 | [6 empty] | 255 |  | 0
2023-03-08 | 201 | [6 empty] | 0 |  | 0
2023-03-09 | 204 | [6 empty] | 0 |  | 0
2023-03-10 | 194 | [6 empty] | 0 |  | 0
2023-03-11 | 191 | [6 empty] | 0 |  | 0
2023-03-12 | 255 | [6 empty] | 0 |  | 0
2023-03-13 | 215 | [6 empty] | 0 |  | 15
2023-03-14 | 213 | 22 | 33 | <2 | 45 | 5.3 | 1.2 | 0 |  | 0 | 8:30 | Stephen Scott | 2023-03-24 | 2023-03-27
2023-03-15 | 204 | [6 empty] | 301 |  | 0
2023-03-16 | 204 | [6 empty] | 0 |  | 0
2023-03-17 | 196 | [6 empty] | 0 |  | 0
2023-03-18 | 193 | [6 empty] | 0 |  | 0
2023-03-19 | 200 | [6 empty] | 0 |  | 0
2023-03-20 | 197 | [6 empty] | 0 |  | 0
2023-03-21 | 205 | [6 empty] | 417 |  | 0
2023-03-22 | 210 | [6 empty] | 0 |  | 10
2023-03-23 | 197 | [6 empty] | 0 |  | 3
2023-03-24 | 205 | [6 empty] | 0 |  | 5
2023-03-25 | 359 | [6 empty] | 0 |  | 0
2023-03-26 | 262 | [6 empty] | 0 |  | 13
2023-03-27 | 230 | [6 empty] | 0 |  | 0
2023-03-28 | 211 | [6 empty] | 0 |  | 0
2023-03-29 | 228 | [6 empty] | 0 |  | 3
2023-03-30 | 253 | [6 empty] | 0 |  | 12
2023-03-31 | 206 | [6 empty] | 0 |  | 0
2023-04-01 | 196 | [6 empty] | 0 |  | 0
2023-04-02 | 216 | [6 empty] | 0 |  | 0
2023-04-03 | 317 | [6 empty] | 0 |  | 2
2023-04-04 | 247 | [6 empty] | 0 |  | 13
2023-04-05 | 226 | [6 empty] | 0 |  | 0
2023-04-06 | 208 | [6 empty] | 0 |  | 0
2023-04-07 | 212 | [6 empty] | 0 |  | 0
2023-04-08 | 219 | [6 empty] | 0 |  | 0
2023-04-09 | 194 | [6 empty] | 0 |  | 0
2023-04-10 | 212 | 20 | 190 | 1 | 46 | 6.8 | 1.7 | 0 |  | 0 | 8:30AM | Shane White | 2023-04-26 | 2023-05-08
2023-04-11 | 215 | [6 empty] | 0 |  | 0
2023-04-12 | 199 | [6 empty] | 482 |  | 0
2023-04-13 | 203 | [6 empty] | 0 |  | 0
2023-04-14 | 203 | [6 empty] | 0 |  | 0
2023-04-15 | 207 | [6 empty] | 0 |  | 0
2023-04-16 | 213 | [6 empty] | 0 |  | 0
2023-04-17 | 209 | [6 empty] | 0 |  | 0
2023-04-18 | 267 | [6 empty] | 225 |  | 0
2023-04-19 | 202 | [6 empty] | 0 |  | 0
2023-04-20 | 198 | [6 empty] | 0 |  | 5
2023-04-21 | 240 | [6 empty] | 0 |  | 7
2023-04-22 | 219 | [6 empty] | 0 |  | 0
2023-04-23 | 223 | [6 empty] | 0 |  | 11
2023-04-24 | 234 | [6 empty] | 0 |  | 6
2023-04-25 | 231 | [6 empty] | 0 |  | 8
2023-04-26 | 238 | [6 empty] | 0 |  | 5
2023-04-27 | 236 | [6 empty] | 0 |  | 8
2023-04-28 | 219 | [6 empty] | 0 |  | 0
2023-04-29 | 214 | [6 empty] | 0 |  | 0
2023-04-30 | 209 | [6 empty] | 0 |  | 0
2023-05-01 | 205 | [6 empty] | 0 |  | 0
2023-05-02 | 196 | [6 empty] | 0 |  | 0
2023-05-03 | 206 | [6 empty] | 0 |  | 0
2023-05-04 | 197 | [6 empty] | 0 |  | 0
2023-05-05 | 188 | [6 empty] | 0 |  | 0
2023-05-06 | 194 | [6 empty] | 0 |  | 0
2023-05-07 | 195 | [6 empty] | 0 |  | 0
2023-05-08 | 202 | [6 empty] | 0 |  | 0
2023-05-09 | 205 | 12 | 32 | 1 | 31 | 6.5 | 1.4 | 0 |  | 0 | 10:00AM | Stephen Scott | 2023-05-09 | 2023-06-02
2023-05-10 | 190 | [6 empty] | 108 |  | 0
2023-05-11 | 193 | [6 empty] | 0 |  | 0
2023-05-12 | 206 | [6 empty] | 0 |  | 3
2023-05-13 | 208 | [6 empty] | 0 |  | 0
2023-05-14 | 371 | [6 empty] | 0 |  | 15
2023-05-15 | 830 | [6 empty] | 0 |  | 50
2023-05-16 | 341 | [6 empty] | 0 |  | 7
2023-05-17 | 268 | [6 empty] | 0 |  | 1
2023-05-18 | 249 | [6 empty] | 0 |  | 0
2023-05-19 | 235 | [6 empty] | 0 |  | 0
2023-05-20 | 233 | [6 empty] | 0 |  | 0
2023-05-21 | 227 | [6 empty] | 0 |  | 0
2023-05-22 | 217 | [6 empty] | 0 |  | 0
2023-05-23 | 238 | [6 empty] | 0 |  | 0
2023-05-24 | 200 | [6 empty] | 0 |  | 0
2023-05-25 | 190 | [6 empty] | 0 |  | 0
2023-05-26 | 189 | [6 empty] | 0 |  | 0
2023-05-27 | 287 | [6 empty] | 0 |  | 0
2023-05-28 | 219 | [6 empty] | 0 |  | 0
2023-05-29 | 230 | [6 empty] | 0 |  | 0
2023-05-30 | 212 | [6 empty] | 0 |  | 0
2023-05-31 | 193 | [6 empty] | 0 |  | 0
2023-06-01 | 212 | [6 empty] | 0 |  | 0
2023-06-02 | 193 | [6 empty] | 242 |  | 0
2023-06-03 | 191 | [6 empty] | 0 |  | 0
2023-06-04 | 218 | [6 empty] | 0 |  | 0
2023-06-05 | 219 | [6 empty] | 0 |  | 3
2023-06-06 | 225 | 12 | 330 | 2.9 | 35 | 10 | 2.1 | 0 |  | 2 | 8:15AM | Stephen Scott | 2023-06-19 | 2023-07-10
2023-06-07 | 210 | [6 empty] | 0 |  | 0
2023-06-08 | 220 | [6 empty] | 0 |  | 0
2023-06-09 | 210 | [6 empty] | 0 |  | 0
2023-06-10 | 201 | [6 empty] | 0 |  | 0
2023-06-11 | 214 | [6 empty] | 0 |  | 0
2023-06-12 | 204 | [6 empty] | 0 |  | 0
2023-06-13 | 210 | [6 empty] | 0 |  | 0
2023-06-14 | 204 | [6 empty] | 0 |  | 0
2023-06-15 | 164 | [6 empty] | 219 |  | 0
2023-06-16 | 179 | [6 empty] | 0 |  | 0
2023-06-17 | 200 | [6 empty] | 0 |  | 0
2023-06-18 | 192 | [6 empty] | 0 |  | 0
2023-06-19 | 173 | [6 empty] | 0 |  | 0
2023-06-20 | 167 | [6 empty] | 0 |  | 0
2023-06-21 | 237 | [6 empty] | 0 |  | 0
2023-06-22 | 206 | [6 empty] | 0 |  | 1
2023-06-23 | 191 | [6 empty] | 0 |  | 0
2023-06-24 | 206 | [6 empty] | 0 |  | 0
2023-06-25 | 207 | [6 empty] | 0 |  | 0
2023-06-26 | 187 | [6 empty] | 0 |  | 0
2023-06-27 | 197 | [6 empty] | 0 |  | 0
2023-06-28 | 195 | [6 empty] | 0 |  | 0
2023-06-29 | 202 | [6 empty] | 0 |  | 0
2023-06-30 | 199 | [6 empty] | 0 |  | 0
14

## 23-24
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 23/24
EPA Licence Number: 351 - Box Ridge Road Coraki
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Sample Collected By | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
2023-07-01 | 157 | [6 empty] | 0 |  | 0
2023-07-02 | 173 | [6 empty] | 0 |  | 0
2023-07-03 | 270 | [6 empty] | 0 |  | 14
2023-07-04 | 270 | 16 | 440 | 1 | 28 | 14 | 14 | 0 |  | 0 | 8:00 | Stephen Scott | 2023-07-14 | 2023-07-25
2023-07-05 | 222 | [6 empty] | 0 |  | 0
2023-07-06 | 196 | [6 empty] | 0 |  | 0
2023-07-07 | 195 | [6 empty] | 0 |  | 0
2023-07-08 | 191 | [6 empty] | 0 |  | 0
2023-07-09 | 204 | [6 empty] | 0 |  | 0
2023-07-10 | 200 | [6 empty] | 0 |  | 0
2023-07-11 | 169 | [6 empty] | 0 |  | 0
2023-07-12 | 159 | [6 empty] | 0 |  | 0
2023-07-13 | 167 | [6 empty] | 0 |  | 0
2023-07-14 | 167 | [6 empty] | 0 |  | 0
2023-07-15 | 166 | [6 empty] | 0 |  | 0
2023-07-16 | 183 | [6 empty] | 0 |  | 0
2023-07-17 | 170 | [6 empty] | 0 |  | 3
2023-07-18 | 258 | [6 empty] | 0 |  | 0
2023-07-19 | 208 | [6 empty] | 0 |  | 0
2023-07-20 | 202 | [6 empty] | 426 |  | 0
2023-07-21 | 168 | [6 empty] | 0 |  | 0
2023-07-22 | 169 | [6 empty] | 0 |  | 0
2023-07-23 | 162 | [6 empty] | 0 |  | 3
2023-07-24 | 263 | [6 empty] | 0 |  | 0
2023-07-25 | 213 | [6 empty] | 0 |  | 0
2023-07-26 | 204 | [6 empty] | 0 |  | 0
2023-07-27 | 177 | [6 empty] | 0 |  | 0
2023-07-28 | 267 | [6 empty] | 0 |  | 0
2023-07-29 | 183 | [6 empty] | 0 |  | 0
2023-07-30 | 172 | [6 empty] | 0 |  | 0
2023-07-31 | 159 | [6 empty] | 0 |  | 0
2023-08-01 | 158 | 17 | 200 | 1 | 32 | 17 | 3.1 | 0 |  | 0 | 9.00am | Stephen Scott | 2023-08-11 | 2023-10-06
2023-08-02 | 264 | [6 empty] | 0 |  | 0
2023-08-03 | 208 | [6 empty] | 0 |  | 0
2023-08-04 | 192 | [6 empty] | 0 |  | 0
2023-08-05 | 186 | [6 empty] | 0 |  | 0
2023-08-06 | 198 | [6 empty] | 0 |  | 2
2023-08-07 | 189 | [6 empty] | 0 |  | 4
2023-08-08 | 193 | [6 empty] | 0 |  | 0
2023-08-09 | 211 | [6 empty] | 0 |  | 0
2023-08-10 | 194 | [6 empty] | 0 |  | 0
2023-08-11 | 194 | [6 empty] | 0 |  | 0
2023-08-12 | 189 | [6 empty] | 0 |  | 0
2023-08-13 | 195 | [6 empty] | 0 |  | 0
2023-08-14 | 174 | [6 empty] | 316 |  | 0
2023-08-15 | 197 | [6 empty] | 0 |  | 1
2023-08-16 | 203 | [6 empty] | 0 |  | 0
2023-08-17 | 199 | [6 empty] | 0 |  | 6
2023-08-18 | 188 | [6 empty] | 0 |  | 0
2023-08-19 | 198 | [6 empty] | 0 |  | 0
2023-08-20 | 191 | [6 empty] | 0 |  | 0
2023-08-21 | 196 | [6 empty] | 0 |  | 0
2023-08-22 | 189 | [6 empty] | 470 |  | 0
2023-08-23 | 178 | [6 empty] | 0 |  | 0
2023-08-24 | 178 | [6 empty] | 0 |  | 0
2023-08-25 | 202 | [6 empty] | 0 |  | 0
2023-08-26 | 187 | [6 empty] | 0 |  | 0
2023-08-27 | 185 | [6 empty] | 0 |  | 0
2023-08-28 | 190 | [6 empty] | 0 |  | 0
2023-08-29 | 189 | 12 | 83 | 1 | 56 | 13 | 1.5 | 0 |  | 0 | 9.45 AM | Stephen Scott | 2023-09-12 | 2023-10-06
2023-08-30 | 200 | [6 empty] | 420 |  | 0
2023-08-31 | 164 | [6 empty] | 0 |  | 7
2023-09-01 | 187 | [6 empty] | 0 |  | 0
2023-09-02 | 175 | [6 empty] | 0 |  | 0
2023-09-03 | 204 | [6 empty] | 0 |  | 0
2023-09-04 | 175 | [6 empty] | 0 |  | 0
2023-09-05 | 184 | [6 empty] | 0 |  | 0
2023-09-06 | 205 | [6 empty] | 0 |  | 0
2023-09-07 | 166 | [6 empty] | 0 |  | 0
2023-09-08 | 150 | [6 empty] | 0 |  | 0
2023-09-09 | 150 | [6 empty] | 0 |  | 0
2023-09-10 | 246 | [6 empty] | 0 |  | 0
2023-09-11 | 151 | [6 empty] | 0 |  | 0
2023-09-12 | 184 | [6 empty] | 0 |  | 0
2023-09-13 | 244 | [6 empty] | 322 |  | 0
2023-09-14 | 182 | [6 empty] | 0 |  | 0
2023-09-15 | 156 | [6 empty] | 0 |  | 0
2023-09-16 | 174 | [6 empty] | 0 |  | 0
2023-09-17 | 207 | [6 empty] | 0 |  | 0
2023-09-18 | 230 | [6 empty] | 0 |  | 0
2023-09-19 | 160 | [6 empty] | 0 |  | 0
2023-09-20 | 147 | [6 empty] | 321 |  | 0
2023-09-21 | 254 | [6 empty] | 0 |  | 0
2023-09-22 | 181 | [6 empty] | 160 |  | 0
2023-09-23 | 183 | [6 empty] | 0 |  | 0
2023-09-24 | 200 | [6 empty] | 0 |  | 0
2023-09-25 | 203 | 4 | 99 | 1 | 46 | 12 | 1.2 | 0 |  | 0 | 11.30AM | Stephen Scott | 05.10.2023 | 06.10.2023
2023-09-26 | 187 | [6 empty] | 0 |  | 0
2023-09-27 | 195 | [6 empty] | 0 |  | 0
2023-09-28 | 225 | [6 empty] | 529 |  | 0
2023-09-29 | 210 | [6 empty] | 0 |  | 19
2023-09-30 | 204 | [6 empty] | 0 |  | 0
2023-10-01 | 193 | [6 empty] | 0 |  | 0
2023-10-02 | 194 | [6 empty] | 0 |  | 0
2023-10-03 | 190 | [6 empty] | 0 |  | 0
2023-10-04 | 184 | [6 empty] | 137 |  | 0
2023-10-05 | 169 | [6 empty] | 0 |  | 0
2023-10-06 | 183 | [6 empty] | 0 |  | 0
2023-10-07 | 181 | [6 empty] | 0 |  | 0
2023-10-08 | 212 | [6 empty] | 0 |  | 0
2023-10-09 | 201 | [6 empty] | 0 |  | 12
2023-10-10 | 195 | [6 empty] | 0 |  | 0
2023-10-11 | 195 | [6 empty] | 0 |  | 0
2023-10-12 | 191 | [6 empty] | 195 |  | 0
2023-10-13 | 187 | [6 empty] | 0 |  | 0
2023-10-14 | 209 | [6 empty] | 0 |  | 0
2023-10-15 | 214 | [6 empty] | 0 |  | 0
2023-10-16 | 191 | [6 empty] | 0 |  | 0
2023-10-17 | 192 | [6 empty] | 0 |  | 0
2023-10-18 | 185 | [6 empty] | 577 |  | 0
2023-10-19 | 185 | [6 empty] | 0 |  | 0
2023-10-20 | 190 | [6 empty] | 0 |  | 0
2023-10-21 | 186 | [6 empty] | 0 |  | 0
2023-10-22 | 192 | [6 empty] | 0 |  | 0
2023-10-23 | 188 | 43 | 240 | 3.1 | 260 | 27 | 2.6 | 0 |  | 0 | 12.00 PM | Adriano Martinez | 2023-11-03 | 2023-11-03
2023-10-24 | 185 | [6 empty] | 535 |  | 0
2023-10-25 | 181 | [6 empty] | 0 |  | 0
2023-10-26 | 221 | [6 empty] | 235 |  | 0
2023-10-27 | 575 | [6 empty] | 0 |  | 42
2023-10-28 | 265 | [6 empty] | 0 |  | 0
2023-10-29 | 233 | [6 empty] | 0 |  | 0
2023-10-30 | 203 | [6 empty] | 0 |  | 0
2023-10-31 | 196 | [6 empty] | 0 |  | 0
2023-11-01 | 198 | [6 empty] | 0 |  | 0
2023-11-02 | 194 | [6 empty] | 0 |  | 0
2023-11-03 | 245 | [6 empty] | 0 |  | 0
2023-11-04 | 256 | [6 empty] | 0 |  | 18
2023-11-05 | 156 | [6 empty] | 0 |  | 0
2023-11-06 | 410 | [6 empty] | 0 |  | 45
2023-11-07 | 264 | [6 empty] | 0 |  | 0
2023-11-08 | 230 | [6 empty] | 0 |  | 0
2023-11-09 | 215 | [6 empty] | 0 |  | 0
2023-11-10 | 303 | [6 empty] | 0 |  | 0
2023-11-11 | 280 | [6 empty] | 0 |  | 18
2023-11-12 | 238 | [6 empty] | 0 |  | 0
2023-11-13 | 216 | [6 empty] | 0 |  | 0
2023-11-14 | 212 | [6 empty] | 0 |  | 0
2023-11-15 | 215 | [6 empty] | 540 |  | 0
2023-11-16 | 208 | [6 empty] | 0 |  | 0
2023-11-17 | 221 | [6 empty] | 0 |  | 0
2023-11-18 | 199 | [6 empty] | 0 |  | 0
2023-11-19 | 202 | [6 empty] | 0 |  | 0
2023-11-20 | 213 | 20 | 17 | 1 | 44 | 6.7 | 1.3 | 0 |  | 0 | 0.5 | Shane White | 2023-12-06 | 2023-12-15
2023-11-21 | 254 | [6 empty] | 0 |  | 8
2023-11-22 | 218 | [6 empty] | 0 |  | 0
2023-11-23 | 209 | [6 empty] | 0 |  | 0
2023-11-24 | 206 | [6 empty] | 0 |  | 0
2023-11-25 | 208 | [6 empty] | 0 |  | 0
2023-11-26 | 209 | [6 empty] | 0 |  | 0
2023-11-27 | 323 | [6 empty] | 0 |  | 0
2023-11-28 | 275 | [6 empty] | 0 |  | 13
2023-11-29 | 236 | [6 empty] | 0 |  | 3
2023-11-30 | 213 | [6 empty] | 0 |  | 1
2023-12-01 | 168 | [6 empty] | 0 |  | 0
2023-12-02 | 227 | [6 empty] | 0 |  | 0
2023-12-03 | 194 | [6 empty] | 0 |  | 0
2023-12-04 | 189 | [6 empty] | 0 |  | 0
2023-12-05 | 202 | [6 empty] | 0 |  | 0
2023-12-06 | 196 | [6 empty] | 554 |  | 0
2023-12-07 | 193 | [6 empty] | 509 |  | 0
2023-12-08 | 205 | [6 empty] | 0 |  | 0
2023-12-09 | 199 | [6 empty] | 0 |  | 0
2023-12-10 | 186 | [6 empty] | 0 |  | 0
2023-12-11 | 221 | 6 | <1 | 2.1 | 43 | 5.1 | 0.93 | 0 |  | 0 | 12:00 | Rebekah McClelland | 2023-12-21 | 2024-01-09
2023-12-12 | 194 | [6 empty] | 0 |  | 0
2023-12-13 | 199 | [6 empty] | 0 |  | 0
2023-12-14 | 171 | [6 empty] | 0 |  | 0
2023-12-15 | 230 | [6 empty] | 0 |  | 17
2023-12-16 | 196 | [6 empty] | 0 |  | 0
2023-12-17 | 185 | [6 empty] | 0 |  | 0
2023-12-18 | 192 | [6 empty] | 0 |  | 0
2023-12-19 | 186 | [6 empty] | 0 |  | 0
2023-12-20 | 197 | [6 empty] | 0 |  | 0
2023-12-21 | 238 | [6 empty] | 0 |  | 2
2023-12-22 | 197 | [6 empty] | 0 |  | 10
2023-12-23 | 205 | [6 empty] | 0 |  | 0
2023-12-24 | 268 | [6 empty] | 0 |  | 0
2023-12-25 | 208 | [6 empty] | 0 |  | 0
2023-12-26 | 213 | [6 empty] | 0 |  | 14
2023-12-27 | 198 | [6 empty] | 0 |  | 0
2023-12-28 | 194 | [6 empty] | 0 |  | 0
2023-12-29 | 193 | [6 empty] | 0 |  | 0
2023-12-30 | 174 | [6 empty] | 0 |  | 0
2023-12-31 | 430 | [6 empty] | 0 |  | 0
2024-01-01 | 225 | [6 empty] | 0 |  | 47
2024-01-02 | 206 | [6 empty] | 0 |  | 0
2024-01-03 | 198 | [6 empty] | 0 |  | 0
2024-01-04 | 192 | [6 empty] | 0 |  | 0
2024-01-05 | 195 | [6 empty] | 0 |  | 0
2024-01-06 | 203 | [6 empty] | 0 |  | 5
2024-01-07 | 192 | [6 empty] | 0 |  | 0
2024-01-08 | 199 | [6 empty] | 0 |  | 0
2024-01-09 | 202 | [6 empty] | 0 |  | 0
2024-01-10 | 204 | [6 empty] | 0 |  | 0
2024-01-11 | 200 | [6 empty] | 0 |  | 2
2024-01-12 | 211 | [6 empty] | 0 |  | 0
2024-01-13 | 213 | [6 empty] | 0 |  | 8
2024-01-14 | 210 | [6 empty] | 0 |  | 0
2024-01-15 | 385 | [6 empty] | 0 |  | 5
2024-01-16 | 298 | [6 empty] | 0 |  | 28
2024-01-17 | 243 | [6 empty] | 0 |  | 3
2024-01-18 | 198 | [6 empty] | 0 |  | 0
2024-01-19 | 201 | [6 empty] | 0 |  | 0
2024-01-20 | 195 | [6 empty] | 0 |  | 0
2024-01-21 | 234 | [6 empty] | 0 |  | 0
2024-01-22 | 215 | [6 empty] | 0 |  | 7
2024-01-23 | 209 | [6 empty] | 0 |  | 0
2024-01-24 | 196 | [6 empty] | 0 |  | 0
2024-01-25 | 191 | [6 empty] | 0 |  | 0
2024-01-26 | 180 | [6 empty] | 0 |  | 0
2024-01-27 | 373 | [6 empty] | 0 |  | 0
2024-01-28 | 485 | [6 empty] | 0 |  | 0
2024-01-29 | 314 | 18 | 1 | 1 | 50 | 7.1 | 1.3 | 0 |  | 40 | 01:00PM | Rebekah McClelland | 2024-02-14 | 2024-02-28
2024-01-30 | 66
2024-01-31 | 421
2024-02-01 | 239
2024-02-02 | 217
2024-02-03 | 222
2024-02-04 | 207
2024-02-05 | 197
2024-02-06 | 189
2024-02-07 | 162
2024-02-08 | 333 | [8 empty] | 3
2024-02-09 | 256 | [8 empty] | 18
2024-02-10 | 204
2024-02-11 | 311
2024-02-12 | 576
2024-02-13 | 266
2024-02-14 | 226
2024-02-15 | 249
2024-02-16 | 231 | [8 empty] | 26
2024-02-17 | 282 | [8 empty] | 3
2024-02-18 | 299
2024-02-19 | 570
2024-02-20 | 1078 | [8 empty] | 60
2024-02-21 | 403
2024-02-22 | 298
2024-02-23 | 264
2024-02-24 | 257
2024-02-25 | 272
2024-02-26 | 254 | 28 | 2 | 1 | 76 | 11 | 2 |  |  |  | 09:00am | Rebeckah McClelland | 2024-03-18 | 2024-04-08
2024-02-27 | 234 | [8 empty] | 4
2024-02-28 | 233
2024-02-29 | 205
2024-03-01 | 231
2024-03-02 | 217
2024-03-03 | 322
2024-03-04 | 322 | [8 empty] | 27
2024-03-05 | 499 | [8 empty] | 11
2024-03-06 | 309
2024-03-07 | 262
2024-03-08 | 242
2024-03-09 | 248
2024-03-10 | 266
2024-03-11 | 279 | [8 empty] | 9
2024-03-12 | 246
2024-03-13 | 234
2024-03-14 | 217
2024-03-15 | 218
2024-03-16 | 211
2024-03-17 | 271
2024-03-18 | 365 | [8 empty] | 11
2024-03-19 | 361 | [8 empty] | 30
2024-03-20 | 268
2024-03-21 | 473 | [8 empty] | 12
2024-03-22 | 338 | [8 empty] | 2
2024-03-23 | 282
2024-03-24 | 268
2024-03-25 | 273 | 8 | 10 | 1 | 39 | 4.9 | 1.3 |  |  | 3 | 08:00am | Shane White | 2024-05-03 | 2024-05-08
2024-03-26 | 1130 | [8 empty] | 10
2024-03-27 | 1167 | [8 empty] | 38
2024-03-28 | 607 | [8 empty] | 6
2024-03-29 | 733
2024-03-30 | 599 | [8 empty] | 10
2024-03-31 | 414
2024-04-01 | 376 | [8 empty] | 2
2024-04-02 | 311
2024-04-03 | 301
2024-04-04 | 2127 | [8 empty] | 112
2024-04-05 | 2182 | [8 empty] | 57
2024-04-06 | 1689 | [8 empty] | 11
2024-04-07 | 1253
2024-04-08 | 899 | [8 empty] | 8
2024-04-09 | 677
2024-04-10 | 548
2024-04-11 | 459
2024-04-12 | 382
2024-04-13 | 377
2024-04-14 | 368
2024-04-15 | 351
2024-04-16 | 330
2024-04-17 | 320
2024-04-18 | 344 | [8 empty] | 10
2024-04-19 | 341
2024-04-20 | 507
2024-04-21 | 2143
2024-04-22 | 2121 | 7 | >2400 | 1 | 27 | 5.5 | 1.5 |  |  | 106 | 9:50am | Stephen Scott | 2024-05-13 | 2024-05-22
2024-04-23 | 1349
2024-04-24 | 940 | [8 empty] | 3
2024-04-25 | 700
2024-04-26 | 571
2024-04-27 | 507
2024-04-28 | 474
2024-04-29 | 485 | [8 empty] | 8
2024-04-30 | 449
2024-05-01 | 451
2024-05-02 | 562 | [8 empty] | 6
2024-05-03 | 1106 | [8 empty] | 13
2024-05-04 | 768 | [8 empty] | 4
2024-05-05 | 660
2024-05-06 | 536 | [8 empty] | 2
2024-05-07 | 1395 | [8 empty] | 18
2024-05-08 | 904 | [8 empty] | 11
2024-05-09 | 881 | [8 empty] | 10
2024-05-10 | 777 | [8 empty] | 6
2024-05-11 | 474 | [8 empty] | 9
2024-05-12 | 1128
2024-05-13 | 804 | [8 empty] | 18
2024-05-14 | 610
2024-05-15 | 570
2024-05-16 | 732 | [8 empty] | 9
2024-05-17 | 1348 | [8 empty] | 19
2024-05-18 | 1186
2024-05-19 | 1218
2024-05-20 | 764 | [8 empty] | 18
2024-05-21 | 622 | 7.2 | 770 | 1 | 42 | 7.4 | 1.6 |  |  |  | 07:30AM | Stephen Scott | 2024-05-31 | 2024-06-05
2024-05-22 | 546
2024-05-23 | 495
2024-05-24 | 456
2024-05-25 | 445
2024-05-26 | 430
2024-05-27 | 407
2024-05-28 | 434 | [8 empty] | 3
2024-05-29 | 454 | [8 empty] | 5
2024-05-30 | 404 | [8 empty] | 4
2024-05-31 | 437
2024-06-01 | 416
2024-06-02 | 467
2024-06-03 | 408 | [8 empty] | 4
2024-06-04 | 375
2024-06-05 | 355
2024-06-06 | 353
2024-06-07 | 298
2024-06-08 | 306
2024-06-09 | 314
2024-06-10 | 338
2024-06-11 | 326
2024-06-12 | 317
2024-06-13 | 308
2024-06-14 | 255
2024-06-15 | 323
2024-06-16 | 321
2024-06-17 | 307 | [8 empty] | 2
2024-06-18 | 290 | 13 | 110 | 1 | 42 | 11 | 2 |  |  |  | 8:00 | Stephen Scott | 2024-07-23
2024-06-19 | 287
2024-06-20 | 278
2024-06-21 | 273
2024-06-22 | 294
2024-06-23 | 300
2024-06-24 | 291
2024-06-25 | 276
2024-06-26 | 281
2024-06-27 | 273
2024-06-28 | 281
2024-06-29 | 287
2024-06-30 | 296

## 24-25
CORAKI SEWERAGE TREATMENT PLANT LICENCE REPORTING 23/24
EPA Licence Number: 351 - Box Ridge Road Coraki
www.epa.nsw.gov.au/prpoeoapp/viewpoeolicence.aspx?docid=32248&sysuid=1&licid=351
DATE | EPA Point 2 Total volume monitoring (Rising main prior to inlet works) | EPA Point 3 Effluent Quality Monitoring | [5 empty] | EPA Point 4 Total volume of effluent reuse | EPA Point 5 Reuse Effluent Quality Monitoring |  | Time Sample Collected | Sample Collected By | Date analysis results obtained | Date Published | Details of Non-compliance
|  | BOD | Faecal Coliforms | Oil and Grease | Suspended Solids | Total Nitrogen | Total Phosphorus |  | Faecal Coliforms | Rainfall
| kL/Day | mg/L | CFU/100mL | mg/L | mg/L | mg/L | mg/L | kL/Day | CFU/100mL | mm
Licence 100 percentile | 1296 | 20 | - | 10 | 30 | - | - | - | 2000 | -
AMT 90 percentile | - | - | - | - | - | - | - | - | 1000 | -
Monday, 1 July 2024 | 280 | [6 empty] | 0 |  | 3
Tuesday, 2 July 2024 | 418 | [6 empty] | 0 |  | 7
2024-07-03 | 834 | [6 empty] | 0 |  | 28
2024-07-04 | 693 | [6 empty] | 0 |  | 10
2024-07-05 | 815 | [6 empty] | 0 |  | 8
2024-07-06 | 791 | [6 empty] | 0 |  | 10
2024-07-07 | 1029 | [6 empty] | 0 |  | 0
2024-07-08 | 748 | [6 empty] | 0 |  | 17
2024-07-09 | 612 | [6 empty] | 0 |  | 0
2024-07-10 | 541 | [6 empty] | 0 |  | 0
2024-07-11 | 477 | [6 empty] | 0 |  | 0
2024-07-12 | 431 | [6 empty] | 0 |  | 0
2024-07-13 | 399 | [6 empty] | 0 |  | 0
2024-07-14 | 387 | [6 empty] | 0 |  | 0
2024-07-15 | 354 | [6 empty] | 0 |  | 0
2024-07-16 | 334 | 6.3 | 2780 | 1 | 39 | 14.8 | 2.52 | 0 |  | 0 | 8:30am | Stephen Scott | 2024-07-25
2024-07-17 | 327 | [6 empty] | 0 |  | 0
2024-07-18 | 317 | [6 empty] | 0 |  | 0
2024-07-19 | 314 | [6 empty] | 0 |  | 0
2024-07-20 | 325 | [8 empty] | 0
2024-07-21 | 299 | [6 empty] | 0 |  | 0
2024-07-22 | 306 | [6 empty] | 0 |  | 0
2024-07-23 | 285 | [6 empty] | 0 |  | 3
2024-07-24 | 292 | [6 empty] | 0 |  | 0
2024-07-25 | 284 | [6 empty] | 0 |  | 0
2024-07-26 | 212 | [6 empty] | 0 |  | 0
2024-07-27 | 346 | [6 empty] | 0 |  | 3
2024-07-28 | 301
2024-07-29 | 280
2024-07-30 | 277
2024-07-31 | 278
2024-08-01 | 275
2024-08-02 | 256
2024-08-03 | 266
2024-08-04 | 283
2024-08-05 | 268
2024-08-06 | 262
2024-08-07 | 258
2024-08-08 | 260
2024-08-09 | 253
2024-08-10 | 261
2024-08-11 | 404 | [8 empty] | 117
2024-08-12 | 2122 | [8 empty] | 73
2024-08-13 | 1800 | 9.85 | 3300 | 3 | 36 | 14 | 2.2 |  |  | 8 | 8:20am | Stephen Scott | 2024-08-22
2024-08-14 | 1634 | [8 empty] | 8
2024-08-15 | 1077 | [8 empty] | 1
2024-08-16 | 808
2024-08-17 | 649 | [8 empty] | 2
2024-08-18 | 535
2024-08-19 | 466
2024-08-20 | 422
2024-08-21 | 427
2024-08-22 | 399
2024-08-23 | 368
2024-08-24 | 373
2024-08-25 | 368
2024-08-26 | 447
2024-08-27 | 362
2024-08-28 | 337
2024-08-29 | 332
2024-08-30 | 327
2024-08-31 | 313
2024-09-01 | 305
2024-09-02 | 299
2024-09-03 | 299
2024-09-04 | 298
2024-09-05 | 297
2024-09-06 | 291
2024-09-07 | 299
2024-09-08 | 288
2024-09-09 | 315 | 5.45 | 1 | 2 | 18 | 10.9 | 2.17 |  |  | 17 | 3:20pm | Stephen Scott | 2024-09-26
2024-09-10 | 300
2024-09-11 | 296
2024-09-12 | 344
2024-09-13 | 310 | [8 empty] | 10
2024-09-14 | 323
2024-09-15 | 308 | [8 empty] | 2
2024-09-16 | 297
2024-09-17 | 294
2024-09-18 | 288
2024-09-19 | 272
2024-09-20 | 272
2024-09-21 | 277
2024-09-22 | 274
2024-09-23 | 266
2024-09-24 | 275
2024-09-25 | 253
2024-09-26 | 294
2024-09-27 | 1293 | [8 empty] | 28
2024-09-28 | 2146 | [8 empty] | 45
2024-09-29 | 1760 | [8 empty] | 111
2024-09-30 | 1051 | [8 empty] | 8
2024-10-01 | 801
2024-10-02 | 636 | [8 empty] | 4
2024-10-03 | 557
2024-10-04 | 487
2024-10-05 | 432
2024-10-06 | 377
2024-10-07 | 353
2024-10-08 | 338 | 11.4 | 300 | 1 | 38 | 9.9 | 2.23 |  |  |  | 8:00am | Stephen Scott | 2024-10-17
2024-10-09 | 403 | [8 empty] | 34
2024-10-10 | 1013
2024-10-11 | 590
2024-10-12 | 510
2024-10-13 | 612
2024-10-14 | 493
2024-10-15 | 442 | [8 empty] | 3
2024-10-16 | 428 | [8 empty] | 6
2024-10-17 | 417
2024-10-18 | 387
2024-10-19 | 372
2024-10-20 | 358
2024-10-21 | 340
2024-10-22 | 340 | 7.2 | 30 | 4.65 | 36 | 8.28 | 1.35 |  |  |  | 7:00am | Craig Smith | 2024-11-14
2024-10-23 | 344
2024-10-24 | 336
2024-10-25 | 358 | [8 empty] | 8
2024-10-26 | 322
2024-10-27 | 313
2024-10-28 | 300
2024-10-29 | 290
2024-10-30 | 298
2024-10-31 | 292 | [8 empty] | 2
2024-11-01 | 289
2024-11-02 | 300
2024-11-03 | 302 | [8 empty] | 6
2024-11-04 | 307
2024-11-05 | 313
2024-11-06 | 284
2024-11-07 | 266
2024-11-08 | 278
2024-11-09 | 275
2024-11-10 | 205 | [8 empty] | 33
2024-11-11 | 515 | [8 empty] | 42
2024-11-12 | 967
2024-11-13 | 834 | [8 empty] | 24
2024-11-14 | 708
2024-11-15 | 463
2024-11-16 | 442
2024-11-17 | 397
2024-11-18 | 383 | [8 empty] | 20
2024-11-19 | 576 | 8.8 | 400 | 3.25 | 58 | 7.96 | 1.49 |  |  |  | 7:30am | Stephen Scott | 2024-11-28
2024-11-20 | 592
2024-11-21 | 585 | [8 empty] | 9
2024-11-22 | 555 | [8 empty] | 5
2024-11-23 | 551 | [8 empty] | 3
2024-11-24 | 479
2024-11-25 | 392
2024-11-26 | 367
2024-11-27 | 358
2024-11-28 | 321
2024-11-29 | 323
2024-11-30 | 353
2024-12-01 | 532
2024-12-02 | 428 | [8 empty] | 26
2024-12-03 | 370 | 6.8 | 10 | 3.19 | 35 | 7.55 | 0.87 |  |  | 3 | 7:20am | Stephen Scott | 2024-12-20
2024-12-04 | 347
2024-12-05 | 374
2024-12-06 | 336
2024-12-07 | 313
2024-12-08 | 270 | [8 empty] | 21
2024-12-09 | 512 | [8 empty] | 38
2024-12-10 | 1182 | [8 empty] | 5
2024-12-11 | 595
2024-12-12 | 444
2024-12-13 | 376
2024-12-14 | 385
2024-12-15 | 378
2024-12-16 | 334 | [8 empty] | 6
2024-12-17 | 438 | [8 empty] | 14
2024-12-18 | 420
2024-12-19 | 362
2024-12-20 | 358
2024-12-21 | 361
2024-12-22 | 345
2024-12-23 | 313
2024-12-24 | 334
2024-12-25 | 309
2024-12-26 | 332
2024-12-27 | 298
2024-12-28 | 275
2024-12-29 | 284
2024-12-30 | 274
2024-12-31 | 262
2025-01-01 | 271
2025-01-02 | 285
2025-01-03 | 264
2025-01-04 | 254
2025-01-05 | 241
2025-01-06 | 252
2025-01-07 | 245
2025-01-08 | 289 | [8 empty] | 18
2025-01-09 | 288 | [8 empty] | 9
2025-01-10 | 263 | [8 empty] | 3
2025-01-11 | 366
2025-01-12 | 498 | [8 empty] | 46
2025-01-13 | 417 | [8 empty] | 2
2025-01-14 | 329 | 18.7 | 100 | 2.35 | 80 | 9.25 | 1.54 |  |  |  | 7:30am | Stephen Scott | 2025-01-14 | 2025-01-31
2025-01-15 | 322 | [8 empty] | 5
2025-01-16 | 311
2025-01-17 | 281
2025-01-18 | 339
2025-01-19 | 355 | [8 empty] | 15
2025-01-20 | 297
2025-01-21 | 285
2025-01-22 | 269
2025-01-23 | 443 | [8 empty] | 29
2025-01-24 | 323
2025-01-25 | 274
2025-01-26 | 275
2025-01-27 | 275
2025-01-28 | 260
2025-01-29 | 276
2025-01-30 | 240
2025-01-31 | 245
2025-02-01 | 261 | [8 empty] | 3
2025-02-02 | 250 | [8 empty] | 6
2025-02-03 | 275
2025-02-04 | 257
2025-02-05 | 242
2025-02-06 | 238
2025-02-07 | 235
2025-02-08 | 249
2025-02-09 | 262
2025-02-10 | 250 | 22.7 | 60 | 7.8 | 81 | 8.76 | 1.55 |  |  |  | 8:15 | Stephen Scott | 2025-02-21
2025-02-11 | 249
2025-02-12 | 276
2025-02-13 | 1743
2025-02-14 | 614
2025-02-15 | 425
2025-02-16 | 359
2025-02-17 | 322
2025-02-18 | 308
2025-02-19 | 305
2025-02-20 | 280
2025-02-21 | 301
2025-02-22 | 284
2025-02-23 | 281
2025-02-24 | 272
2025-02-25 | 270
2025-02-26 | 259
2025-02-27
2025-02-28 | 262 | [8 empty] | 95
2025-03-01 | 284
2025-03-02 | 270
2025-03-03 | 249
2025-03-04 | 290
2025-03-05 | 372
2025-03-06 | 533
2025-03-07 | 2196
2025-03-08 | 2231
2025-03-09 | 2136
2025-03-10 | 2082
2025-03-11 | 2084
2025-03-12 | 2157
2025-03-13 | 2184 | 8.1 | 5500 | 10.4 | 28 | 6 | 2.17 |  |  |  | 8:00 | Stephen Scott | 2025-04-01
2025-03-14 | 2234
2025-03-15 | 2259
2025-03-16 | 946
2025-03-17 | 592
2025-03-18 | 515
2025-03-19 | 499
2025-03-20 | 475
2025-03-21 | 442
2025-03-22 | 439
2025-03-23 | 413
2025-03-24 | 469
2025-03-25 | 527
2025-03-26 | 1046
2025-03-27 | 1725
2025-03-28 | 2076
2025-03-29 | 1899
2025-03-30 | 1187
2025-03-31 | 798
2025-04-01 | 626
2025-04-02 | 1456
2025-04-03 | 2170
2025-04-04 | 1353
2025-04-05 | 946
2025-04-06 | 732
2025-04-07 | 615 | 4 | 100 | 2 | 43 | 2.99 | 0.39 |  |  |  | 12:00 | Stephen Scott | 2025-04-30
2025-04-08 | 557
2025-04-09 | 536
2025-04-10 | 536
2025-04-11 | 841
2025-04-12 | 1123
2025-04-13 | 1863
2025-04-14 | 1057
2025-04-15 | 1032
2025-04-16 | 904
2025-04-17 | 691
2025-04-18 | 606
2025-04-19 | 530
2025-04-20 | 497
2025-04-21 | 516
2025-04-22 | 503
2025-04-23 | 473
2025-04-24 | 594
2025-04-25 | 1692
2025-04-26 | 2085
2025-04-27 | 1482
2025-04-28 | 883
2025-04-29 | 697
2025-04-30 | 613
2025-05-01 | 572
2025-05-02 | 665
2025-05-03 | 753
2025-05-04 | 737
2025-05-05 | 1626 | 5.35 | 10 | 1 | 46 | 5.28 | 0.91 |  |  |  | 14:00 | Rebekah McClelland | 2025-05-16
2025-05-06 | 1061
2025-05-07 | 800
2025-05-08 | 662
2025-05-09 | 1180
2025-05-10 | 1182
2025-05-11 | 1114
2025-05-12 | 1736
2025-05-13 | 1725
2025-05-14 | 1522
2025-05-15 | 1699
2025-05-16 | 1363
2025-05-17 | 1891
2025-05-18 | 1105
2025-05-19 | 934
2025-05-20 | 780
2025-05-21 | 679
2025-05-22 | 632
2025-05-23 | 577
2025-05-24 | 530
2025-05-25 | 505
2025-05-26 | 482
2025-05-27 | 467
2025-05-28 | 434
2025-05-29 | 424
2025-05-30 | 685
2025-05-31 | 2069
2025-06-01 | 1162
2025-06-02 | 963
2025-06-03 | 1165
2025-06-04 | 861
2025-06-05 | 744
2025-06-06 | 630
2025-06-07 | 580
2025-06-08 | 540
2025-06-09 | 496
2025-06-10 | 461
2025-06-11 | 444
2025-06-12
2025-06-13
2025-06-14
2025-06-15
2025-06-16
2025-06-17
2025-06-18
2025-06-19
2025-06-20
2025-06-21
2025-06-22
2025-06-23
2025-06-24
2025-06-25
2025-06-26
2025-06-27
2025-06-28
2025-06-29
2025-06-30